## X 02-06
REHAPETILATION EQUIPMENT
Equipment :
Electric submersible darning sewage pump water cooled motor
Code | Capacity M3/MIN | Head M | Speed R.P.M | Power KW | Volt V | Qty.
02-06-00001 | 0.15-0.1 | 0.365015-0.4 | 3000 | 1.5 | 220 or 380V 50 HZ | 150
02-06-00002 | 1 | 10 | 3000 | 3.7 | 220 or 380V 50 HZ | 200
02-06-00003 | 0.5 | 15 | 3000 | 3.7 | 220 or 380V 50 HZ | 140
02-06-00004 | 1 | 22 | 3000 | 7.5 | 220 or 380V 50 HZ | 200
02-06-00005 | Equipment: Package unit |  |  |  |  | 2000
complet witch supply cold air directly by duct to the building.
cap: 20 ton
inside temp : 18 C
380 v. , 3 pH , 50HZ , gas R22
02-06-00006 | Equipment: Air Cooled Chiller |  |  |  |  | 250
Cap : 100 Ton
Ambient Temp. 60C
Water out let Temp 12 C
Water in let temp 6 C
Compress type semi hermetic
Coil materiel : Copper tubes with element fins
Fan type : Propeller
Evaporator : Sheila and tubs
GSA use R-12 or R-22
380 V 50 HZ
02-06-00007 | Equipment: Air Cooled Chiller |  |  |  |  | 250
Cap : 200 Ton
Ambient Temp. 60C
Water out let Temp 12 C
Water in let temp 6 C
Compress type semi hermetic
Coil materiel : Copper tubes with element fins
Fan type : Propeller
Evaporator : Shell and tubs
GSA use R-22 or R12
380 V 50 HZ
02-06-00008 | Equipment: Window type air-condition with heater |  |  |  |  | 25000
Cap : 2 Ton 24000 BTU
GSA R-22
220 V 50 HZ , 3PH
02-06-00009 | Equipment Split Unit with heater |  |  |  |  | 10000
Cap : 2 Ton
GSA R-22
220 V 50 HZ , 24000 BTU
TIRES
02-06-00010 | 600x14 High Quality |  |  |  |  | 4000
02-06-00011 | 650x14 High Quality |  |  |  |  | 5000
02-06-00012 | 700x15 High Quality |  |  |  |  | 6000
02-06-00013 | 750x16 High Quality |  |  |  |  | 5000
02-06-00014 | 205x16 High Quality |  |  |  |  | 6000
02-06-00015 | 650x16 High Quality |  |  |  |  | 2000
02-06-00016 | 1200x20 High Quality |  |  |  |  | 4000
02-06-00017 | 1100x20 High Quality |  |  |  |  | 4000
02-06-00018 | 1200x24 High Quality |  |  |  |  | 1200
02-06-00019 | 1000x20 High Quality |  |  |  |  | 800
Acid batteries
02-06-00020 | 45Amp x12V High Quality |  |  |  |  | 150
02-06-00021 | 60x12 High Quality |  |  |  |  | 1800
02-06-00022 | 75x12 High Quality |  |  |  |  | 300
02-06-00023 | 90x12 High Quality |  |  |  |  | 800
02-06-00024 | 110x12 High Quality |  |  |  |  | 300
02-06-00025 | 130x12 High Quality |  |  |  |  | 1000
02-06-00026 | 180x12 High Quality |  |  |  |  | 800
02-06-00027 | Equipment : Blood bank refrigerator |  |  |  |  | 800
1- internal temp. ranging from +2 C to +8 C at the following ambient conditions :
Summer : DBT 50 C
WBT25C
Winter : DBT 1 C
WBT _3 C
2- Double compressor units for additional safety work with ferine R 12 or R 22
3-inside and outside materil: stinless steel
4-audible/ visual and extenai alarms with battery
Low alarm: 0 C
High alarm: + 10C
5 – Automatic defrosting
6- 7Day recorder
7- 220V, 50HZ, 3PH
Training for 2 engineer two weeks
Spare parts for 5 years
02-06-00028 | Equipment : air compressor |  |  |  |  | 70
Air compressor complete (compressor + motor) with out tank will be suitable to be initialed in the tank of the old model with this information .
Air compressor :
Type LE7 ATLAS COPCO
S.N : AML 107283
Max working pre bar (2)(10)
Max speed R.P.M 1800 , made in sweeden 1983
Motor:
Type LS 112MI
No: 618627, 4KW, 1430 R.P.M
(220 V , 15.2A / 380 V,8.8A) , 50 HZ
training for engineers
spar part for 3 year
complete catalog for maintenance operation and installation
02-06-00029 | Equipment:- cooling tower
| Capacity :150 ton |  |  |  |  | 20
| 200 ton |  |  |  |  | 35
| 100 ton |  |  |  |  | 30
| 50 ton |  |  |  |  | 15
Water temp. 38/ 30 Cْ
Complete cooling tower must be separate motor for each blower and will work in high
Humidity wetter 60 % Humidity and total hardness is for water 500ppm
Recommended spare for 5 years.
Include complete motor
Fin , belt,shaft, spray nozzle , bearing , blower ,
Nozzle , motor complete, ball float valve
Training for engineer and tech.
Complete catalog for spare part and operation maintenance catalog
02-06-00030 | Equipment: Corps refrigerator |  |  |  |  | 320
Walk in freezers to preserve corpses at internal temperature ranging from (+5 deg.) to (-30 deg.)At the following ambient conditions: summer: DBT 50 Deg.
WBT 25 deg.C
Winter: DBT 1 deg.C
WBT -3 deg.C
Internal volume of the store: 3x4x3 M3
Required quantity: freezing stores
A) Construction :
1- Freezers shall be shipped in knock- down sections easy to re- erect
2- Cabinet interior shall be made of heavy corrosion proof aluminum, floor made of heavy gauge anti- slip aluminum
3- Cabinet exterior shall be made of aluminum, coated with a white weather proof coating to make it suitable for out- door installation
4- Insulation shall be sufficient to maintain the specified internal temperature in the specified ambient conditions but shall be not less than 12 cm of polyurethane
5- Door shall be constructed of aluminum and shall have an external lock with keys. Door handle can be operated from inside and outside. Low voltage heater wire strip with electrical control shall be provided. A push- button shall be fitted inside to sound an alarm in case of a person is trapped inside
6- Light- weight shade to protect the cabinet from rain and sun to be fitted on top of it .shape , size and material of shade shall be suggested by the tenterer
7- External dial thermometer must be provided
8- Audio and visual alarm for high temperature must be fitted
9- Sufficient internal lighting automatically switches on when door opens
10- Air curtain by the door operates automatically when door opens
11- The stores shall be equipped with hangers that supports six removable trays which carry the human corpses, these trays shall be positioned on both sides of the stores three at each side . the under must tray shall be positioned within 15 cm from the floor with 75cm distance between the trays the tray dimension shall be 2m length, 75cm width
B) REFRIGERATION SYSTEM
Two independent refrigeration systems shall be installed, each being capable to maintain the required internal temperature at the specified ambient conditions
An automatic alternator clock timer shall be furnished to automatically reverse the sequence of operation of the two systems to assure even wear. And if one system be unable for any reason to maintain the required temperature the second system shall automatically cut-in. Visual indication of the operation and faults of the system shall be shown on the control panel. Capacity and type of compressors used shall be mentioned in the offer. Ferine R12 or R502 used.
The entire system shall utilize heavy-duty refrigeration copper tubing, no aluminum or steel tubing to be used. Evaporator fins shall be anticorrosion type. Automatic electrical defrosts with pipes for drain water must be provided.
C). ELECTRICAL SYSTEM
System shall operate from single - phase, 220V, 50 HZ supply or from three- phase, 4 wire, 380V.
D). SPARE PARTS
An itemized and priced spare parts list sufficient for five years repair and maintenance of the equipment shall be submitted with the offer. The price shall be C & F Baghdad and the spares shall be shipped with the cold stores. Among other things, the list shall include the following items:
No. Description
1- compressor
2- Evaporator motor fan
3- Blades for evaporator
4- condenser motor fan
5- Blades for condenser fan
6- Thermometer
7- Thermostat & alarm thermostat
8- High-low pressure cut out
9- Oil pressure cut out
10- Door gasket with heater
11- Contactor for compressor
12- Relays & electrical switches & klaxon
13- Defrost heaters
14- Automatic electric defrost
15- Automatic alternator for reverse sequence
16- Internal light bulb
17- over load
18- Expansion valve
19- filter drier
20- Fuses of different writings
21- solenoid valve
22- alarm horn
23- micro switch & spare for air curtain
24- operating switches
E). TESTING AND GUARANTEE
Tendered shall guarantee and maintain the freezers for aneroid of two years starting from the date of putting them in operation. All equipment shall be tested and outstanding technical problems shall be discussed & settled in the firm prior to the shipment of the equipment & in the presence of our engineer, tendered shall pay for the return air tickets of our engineer & bear all costs of his stay with the firm including full board & loading for aperiodof tow weeks
F). TRAINING
Tendered shall train two persons on the repair & maintenance of the equipment, each person for aneroid of one month in his firm tendered shall bear all costs including return air tickets full board & lodging and any other expenses.
G). INSTALLATION
Tendered shall make complete installation of all freezers except civil works such as base. Tendered shall supply all materials necessary for the complete installation. Any offer not including complete installation will be rejected.
**NOTE**
Load calculations & photos of freezing stores shall be sent with the offer
02-06-00031 | Equipment : TRANSFORMER |  |  |  |  | 2
220 V - 97 V
02-06-00032 | Equipment : Vegetable and fruit cold stor |  |  |  |  | 600
Cold store for the purpose
Noose walk in cold stores temperature raining from (-5 c) to (+15 c) at the flowing ambient conditions :
summer : DBT 50 C
WBT 25 C
winter : DBT 1C
WBT -3 C
Internal volume : not less than 50 cubic meters
A) construct ion :
1- cold stores shall be shipped in knock – down sections to re-erect
2- cabinet interior shall be made of heavy corrosion proof aluminum, floor made of heavy gauge anti – slip aluminum
3- cabinet exterior shall be made of aluminum , coated with a white weather proof coating to make it suitable for out-door installation
4-In sultan shall be sufficient to maintain the specified internal temperature in the specified ambient condition but shall be not less than 10 cm of polyurethane
5- Door shall be constructed of aluminum & shall have an external lock with keys. Door handle can be operated from inside & outside. Low voltage heater wire strip with electrical control shall be provided. Apish-button shall be fitted inside to sound an alarm in case of person is trapped
6- light- weight shade to protect the cabinet from rain & sun to be fitted on top of it. Shape size & material of shade shall be suggested by the tendered
7- external dial thermometer must be provided
8- Audio & visual alarm for high temperature must be fitted
9- Sufficient internal lighting automatically switches on when door opens
10- air curtain by the door operates automatically when door opens
11- Shelves shall be made of strong galvanized steel positioned on all sides shelves shall be grid type.
B) .REFRIGERATION SYSTEM
Two independent refrigeration system shall be installed each being capable to maintain the required internal temp. at the specified ambient conditions an automatic alternator clock timer shall be furnished to automatically reverse the sequence of operation of the two systems to assure even wear , and if one system be unable for any reason to maintain the required temp. the second system shall automatically cut- in . Visual indication of the operation & faults of the system shall be shown on the control panel. Capacity &type of compressor used shall be mentioned in the offer . the entire system shall utilize heavy duty refrigeration copper tubing , no aluminitium or steel tubing to be used . evaporator fins shall be anticorrosion type . automatic electrical defrost with pipes for drain water must provided .use R12 or R502
C) Electrical system
System shall operate from single – phase , 220V, 50 HZ, supply or from 3 pH , 4 wire , 380 V
D) Spar parts
An itemized and priced spar parts list sufficient for fife years repair & maintenance of the equipment shall be submitted with the offer . the price shall be C&F Baghdad and the spares shall be shipped with the cold stores . among other things , the list shall including the following items.
No. Description
1- compressor
2- Evaporator motor fan
3- Blades for evaporator fan
4- condenser motor fan
5- Blades for condenser fan
6- Thermometer
7- Thermostat & alarm thermostat
8- High-low pressure cut out
9- Oil pressure cut out
10- Door gasket with heater
11- Contactor for compressor
12- Relays & electrical switches & klaxon
13- Defrost heaters
14- Over load
15- expansion valve
16- filter drier
17- fuses
18- solenoid valve
19- alarm horn
20- micro switch &spare for air curtain
21- operating switches
22- alarm horn
23- micro switch & spare for air curtain
24- operating switches
E) TESTING & GURANTEE
tender shall guarantee the cold stores for a period of tow years starting from the date of putting them in operation . all equipment shall be tested & out standing technical problems shall be discussed & settled in the firm prior to the shipment of the equipment & in the presence of our engineer , tender shall pay for the return air tickets of our engineer & bear all costs of his stay of two weeks. All spare parts that will be used by the tendered during these two years shall be on the account of the tendered.
F) Training :-
Tendered shall train two person on the repair and maintenance of the equipment for a period of one month in this firm. Tendered shall bear all costs in clouding air tickets.
G) Installation
Tendered shall make complete installation of all cold stores except civil works such as concrete installation shall be supplied by tendered. Any offer not including complete installation will be rejected>
Notes:-
3- Medicines shall be brought in stores at around 38OC.
2-Quantity of store medicines is not less than 1500 Kg.
3-Load calculations shall be sent with the offer.
02-06-00033 | Equipment : computer |  |  |  |  | 7000
Processor: pentium II 450 MHZ MMX compliant with year 2000 512 Kb cache
Mother board: BX(AGP,PCI,ISA)ATX
RAM: 128 MB
Hard disk : at least 6.2 Gb
CD-ROM :40X EIDE
Sound card : PCI 32 BIT (software wave table)AW5-128
SPEAKERS:180W
Floppy disk : 3.5 “ HD 1.44 Mb
Display adapter : AGP 8 Mb
Monitor : 15” savg 1024 X 768 , 0.28 DPI
Net work card : 10/100 Mb /S ethernet
Fax modem card : 56 (V. 90) fax /modem
Case : mini tower (ATX 250 w)
Key board : A/E 104 KEYS (PS/2 CONN)
Mouse : 2 buttons ( PS/2 CONN.)
Zip drive : iomega internal 100Mb with 100 box containing 100 Mb discettes
CD-RW: CD- writer 2X2X6X with 100 box containing blank CDs
Super disk: internal 120 MB imation atapi IDE inter face with(100)boxes of diskettes
UPS :400VA/250W
Printers :
- DOT matrix : EPSON LQ 2170 arabic
- LaserJet : HP- 6L
- Inkjet (cooler) : HP-DESKJET 1120C
02-06-00034 | Equipment : Softeners |  |  |  |  | 100
Fully automatic softener and meter control
3.NORMAL HYDROLIC GEAR
- Control panel ,Brine tank, with its interconnecting pipe system and all its additional accessories suitable for continuos soft water supply as following:
- Max floweret :- 10 m3/h
- Resin:- strong cationic resin sodium base
- Power supply :- 220V or 380V 50 HZ
- Hardness treated water 0oFTH
- Presume drop :- 8 MWG
- Operating pressure :- 2 to 6 bar
- Recommended spare part for 5 year with complete quantity of exchange resin.
supply complete catalog and drawing electric mechanical spare part and mountenace operation catalog.
- Training for 2 Engineers +2 Technician
02-06-00035 | Equipment : Softeners |  |  |  |  | 100
Fully automatic softener and meter control
- Control panel ,Brine tank, with its interconnecting pipe system and all its additional accessories suitable for continuos soft water supply as following:
| - Max floweret :- 10 m3/h | :-5M3/h
- Resin:- strong cationic resin sodium base
- Power supply :- 220V or 380V 50 HZ
- Hardness treated water 0oFTH
- Presume drop :- 8 MWG
- Operating pressure :- 2 to 6 bar
- Recommended spare part for 5 year with complete quantity of exchange resin.
- Recommended spare part for 5 year with complete quantity of exchange resin.
supply complete catalog and drawing electric mechanical spare part and mountenace operation catalog.
- Training for 2 Engineers +2 Technician
02-06-00036 | Equipment : hospital lift complete
QTY As below
Site:-saddam Medical city general hospital
| 1- hospital standard 24- Passengers Plaint bed, side open door 21 floor Stainless steal doors with all parts need to replace existed lifts (erection and operating) for medical city |  |  |  |  | 2PCS
Qty.
| 2- As above but bed lift 4-Floor for Saddam General Hospital |  |  |  |  | 2PCS
| 3- As above but 6- Passengers 4- Floor for Saddam General Hospital |  |  |  |  | 4PCS
| 4- As above but 6- Passengers 7- Floor center open for Central Child Hospital |  |  |  |  | 6PCS
| 5- As above but bed lift 7- Floor for Central Child Hospital |  |  |  |  | 4PCS
| 6- Cargo lift 2 floors load 4000Kg side opening dons for Basra drug stores |  |  |  |  | 2PCS
| 7- As above but 1400 Kg 7-Floor for Saddam Teaching Hospital in Basra |  |  |  |  | 4PCS
| 8- As above bedlift but 1800 Kg 2- Floor for Tahreer Hospital and Basrah Funeral Hospital. |  |  |  |  | 10PCS
02-06-00037 | Fork Lift (2Ton) |  |  |  |  | 200
1.DIESEL ENGIN 4 CYLINDER WATER COOLED
2.BATTRY 12V
3.NORMAL HYDROLIC GEAR
4.MAX HIGHT 3.5M
02-06-00038 | Absorption chiller |  |  |  |  | 60
550 TON
02-06-00039 | High tension switch gear
| 1-aircircuit breaker 1600A AH-16B |  |  |  |  | 10
| 2-aircircuit breaker 1600A AH-30C |  |  |  |  | 10
3-batery 100V QSC-SOE
4-batery 24V AMH--SOE
5-printed circuit breaker AED-6A
6-printed circuit breaker D2-100
| 7-high VGE oil labricant 11KV |  |  |  |  | 5000LT
02-06-00040 | Paging system |  |  |  |  | 120
1-Complot paging system compressing control station and 5 W transmitter maximum rang less than 1000 m and 100 radio receiver
2-the system should be either independent or interfacing with any type of exchange
3-installation on site for 6-system and training technicians of other sites during installation to install the other system
4-training on factory for 5 engineers for 2 weeks
5-complot sets of manuals installation and manta enamel
6-spare parts for 2 years
7- greenery for one year and one maintenance
02-06-00041 | Equipment: Freezers |  |  |  |  | 1000
Volume : 16 ft3
Temperature: from 00C to -300C.
220V ,50HZ, 1PH
compressor : Tecumseh or Danffos
frion use : R12 or R22
Dial thermometer outside
the door have lock
Inside wall for freezer Aluminum plate.
Freezer has alarm system when temp. low or high
02-06-00042 | Equipment: Vaccines and medicines refrigerator |  |  |  |  | 3000
Volume : 16 ft3
Temperature: from 00C to 300C.
220V ,50HZ, 1PH
compressor : Techumsuh or Danffos
frion use : R12 or R22
Dial thermometer outside
the door have lock
Freezer has alarm system when temp. low or high
Equipment: kitchen equipment
Site:saddam medical city
02-06-00043 | Mobile sink capacity 220 liter dimension 800X600X500mm total high 650 mm |  |  |  |  | 40
02-06-00044 | Mobile sink capacity 220 liter dimension 800X600X500mm total high 650 mm |  |  |  |  | 40
02-06-00045 | Equipment: Steam Boiler for heating (5 ton/hr) |  |  |  |  | 100
A) Steam Boilers
1. The sub-contractor shall provide install, test, and commission one no. packaged steam boiler and associated equipment.
2. The boiler shall be rated capacity of 5000 kg/h with a working pressure of 8-10 bar. Test pressure must be rated 1.5 times working pressure.
3. The packaged boiler shall be manufactured in accordance with either the relevant TRD/DIN (German code) or British standards.
4. The packaged boiler shall be supplied with matched ,forced draught pressure jet burner of high/low flame 2-stage operation, suitable for burning dual fuel 35 second redwood no. 1 at 38 c ,light fuel oil and groping butane and heavy oil .
5. The Boiler burner shall be fully automatic in operation complete with all necessary controls for oil and air supply, flame failure ,ignition ,pre and post purge periods etc. all pre wired to the sensors and boiler control/indication panel.
6. The boiler shall be high efficiency 3-parse Ir. reversed flow type with pressurized combustion chamber.
7. Boiler shall be fully pressure tested at the factory and 1 copy of the manufacturers test certificates (approved by neutral test instate) shall be provided.
8. Flue connection shall be at the rear of the boiler.
9. The packaged boiler shall have duty and stand by feed water pumps with associated automatic controls. pumps shall be of the multistage-centrifugal type.
10. The packaged boiler shall have the following mounting:
1. main steam valve
2. 2-high lift state valve, 5000 kg blowing – off pressure 10 bar
3. pressure gauge.
4. 2-water level gauge.
5. feed water pressure gauge.
6. Burner control sensors.
7. water level /feed pumps controls.
8. pressure control
9. Blow down valve suitable for timed automatic operation in
conduction with timer unit.
10. 2-boiler feeding pumps with electric motor designed specified
boiler capacity at 10 bar.
11. The boiler shall have its own control/indication panel completely premiered with all necessary functions for a central and automatic supervision and control of the boiler unit . The panel shall incorporate all required facilities for correct monitoring and control. All necessary control lamps ,contractors, switches, fuses, lock-out lamps etc. shall be incorporated together with “hours run” meter .
B- BOILER FLUE GAS DUCTING
1. The sub-Contactor shall supply. install and commission flue gas ducting (chimney) terminating in a suitable clown above roof level. Height (above floor level) 5m.
2. The “nominally” horizontal flue gas ducting shall be infect be in stalled “to fall ”,rising slightly ,towards the main vertical chimneys.
3. cleaning access doors shall be provided at the ends of horizontal ducting together with combined pressure release/cleaning door at the base of vertical flue.
4. A condenser drain valve shall be provided from the base of vertical flue ,located at low level, complete with hose connection.
C. BOILER FEED WATER + CONDENSATE TANK INCLUDE. CHEM. DOSING
1. The sub-contractor shall supply ,in stall ,test ,and commission a feed water tank at high level in the plant room supplied as a complete package.
2. The tank shall be constructed of sheet steel with welded joints and will be supplied complete with all necessary channel iron wall and floor supports thickness 5mm.
3. The tank shall have a minimum capacity of 3000 liter's, complete with following features and fittings etc:
1. 500mm bolted access manhole
2. Glass water level gauge.
3. water level control electrodes and associated solenoid valve
for make-up water.
4. Sprague pipes for condense return below water level.
5. spray pipes for direct steam injection below water level for
preheating feed water at boiler start-up, complete with thermostat
icily control valve.
6. vent pipe.
7. all necessary connection.
8. 50 mm thick rigid foil backed fibber glass insulation of 64 kg/m3
density finished in 24 swag aluminum sheeting.
4. The tank shall also have provision for being chemically dosed by Adonis set.
5. The dosing set shall consist of plastic mixing drum with an adjustable rate dosing pump suitable for dosing oxygen scavengers, as recommended by the boiler manufacture or other equal and approved chemical supply suitable for 5 tons of steam supply must be included.
6. The chemical dosing pump set shall be supplied by the boiler manufacture or equal approved.
D. BOILER BLOW DOWN TANK
1. The sub-contractor shall supply ,install, test and commission a boiler blow down tank.
2. The tank shall have a capacity of Hrs supplied as a complete.
3. The tank shall be welded steel construction complete with mounting legs.
4. The tank shall be fitted with an automatic condense aftercare complete with non. return valve ,thermostat and solenoid valve strainer, and globe valve all mounted on the untreated cold water supply to the unit.
5. The after cooler and accessories shall also be supplied by the tank manufacturer.
6. The blow down tank shall be complete with pipe.
E. BOILER BLOWDOWN SYSTEM
1. The boiler shall have its own automatic system to provide for periodic blow down .
2. This shall consist of an electrical activated blow down valve which shall operate under the dictates of timer unit to provide a time controlled cycle as necessary.
3. The timer/control unit shall provide blow down for Emmanuelle adjustable pre-set period at desired intervals which will, again be variable.
4. The boiler blow down system shall be as manufacture boiler manufacturer or equal and approved, and shall be supplied as package for the boiler.
F. WATER SOFTENER PLANT
1. The water softener shall be of the duel type in order to provide feed water for 24 hours/day continuously (No death-time due to regeneration).
2. The water softener must be supplied complete with :
- booster pump(inlet pressure 0.5 bar).
- salt tank(brine tank)
- 2water softener colors complete with control solenoid valves
- filter(strainer)
- contact water meter compel. with water softener control unit
- all armatures
3. The water softener must have capacity at 80-100 litter/h
4. water treatment
water specification:
-total water hardness caco3 150 400
-calcium ca 40 120
-chloride c1 10 70
-sulfate so4 40 120
-pH-valve 6.8 7.6
-Fe 0 0.24
-total alkalinity caco3 110 160
G. Heat exchanger (horizontal type)
with U-copper tubes (extensible) complete with thermal insulation:
-capacity: 450.000 kcal/h
-primary : saturated steam 8 bar
-secondary: water 15-60 c0
-complete with asset of drawings.
H. Heat exchanger (horizontal type)
with U-copper tubes (extensible) complete with insulation:
-capacity : 1.100.000 kcal/h
-primary : saturated steam 8 bar
-secondary water 15-90 c0
complete with a set of drawings.
I. spare parts for 5 years with complete set of fire tube
J. Fuel storage tanks
- content 10.000 Lt.
- wall thickness 5 mm
with tar-coating including supports for air mounting
connections and controls to storage tank:
- 1 filling 1 ½” incl.
- 1 draining 1 1/2" include
- 1 air rent 2” with air
- 1 supply and return
- 1 drain valve 1 1/2” include connection
- 1 supply valve
- 1 manhole 400
- 1 pneumatic fuel gauge
- 1 measuring rod
K. control to fuel supply system (burner accessories) 1 Electro valve ,ventilation system consisting of:
stop cock, oil filter, Electro valve ,air vent flange and for other type of fuel and maintenance
L. operation manual and diagram complete in English with all drawing electronically and mechanical
M. Training
3 engineer and 3 technician for one month at factory
02-06-00046 | EQUIPMENT : STEAM BOILER FOR WASHING (0.6 TON/Hr) |  |  |  |  | 200
Nos. Fuiiy Automatic Multi-Pass Steam boilers with leotrical and mechanical control ,pumps ,safeties with Auxiliaries According to the international standards and regulations for steam boiler under the following specifications :
A. Out put capacity 600kg/Hr
B. Working pressure (6-8) bar
C. Oil burner type l 3 VZ monarch and gas (butane .propane ) and heavy oil
The following item must be included
1.Automatic blow down .contorted by timer
2.Feed/Condense water tank capacity of one meter cube with mechanical float ,water level indicator ,valves. etc,
3. Daily oil tank sand plastid with inner and outer anticorrosion painting ,capacity of lion liters complete with level indicator filling holes and suitable base
4.Oil filter with valve ,strainer, hose of 1/2 outlet diameter and accessories for other type of fuel
5.Suitable chimney 5 meter vertical height
6.Itemized and separately priced spare parts list sufficient for 5 years and maintenance including 2 sets internal pipes for each boiler
7.Suitable automatic water softener plants working on(0.5 bar) domestic water pressure to supply water 8 with zero degree hardness complete with all flexible pipes , electrical equipment's and fittings required and washable sand and clay filter.
8.Test certificate for each boiler sublimed by a reputable specialized firm electricity : 4 lines , 3 phase 380/220 voles , 50 HZ
water supply : 0.5 bar domestic water pressure
Analysis:
-Total hardness as CAE 0.3 400mg /l
-Calcium as ca 120mg/l
-Chloride as CL 70MG/L
-SULFATE AS SO 4 120MG/L
-pH 7.6
-Iron as Fe 0.24 mg/l
-Total alkalinity as cacao 3 160mg/l
9.Rcco mounded spare part list for 5 years with complete set fine tube
10.Supply all electrical and mechanical drawing and maintenance catalog and spare part catalog complete
11.Training for 3 engineers and 3 technician
02-06-00047 | EQUIPMENT : HOT WATER BOILER (1 TON/Hr) |  |  |  |  | 300
roting : 760 000 kcal/hr (879 kw)
working press : 8 bar
design : 3 pass wet back fier tube
burner : dual fuel , LPG and light gasoil
standerd : B.S 2790 and equivalent
quality : 150 9001
full automatic equippede with all necessory controls saftys fittings , valves with
1) 10000 lt fuel tank
2) 5 meters steel chimeny
3) 5- years recommended spare parts
4) 1- year warranty
5) supervision on installation
6) training of MOH engineers in factory
TYRE
02-06-00048 | 600X 14 |  |  |  |  | 2700
02-06-00049 | 700X 15 |  |  |  |  | 1600
02-06-00050 | 750X 16 |  |  |  |  | 5000
02-06-00051 | 1200X 20 |  |  |  |  | 3800
02-06-00052 | 1200X 24 |  |  |  |  | 1600
02-06-00053 | 3007436/007 |  |  |  |  | 126
02-06-00054 | 3007436/004 |  |  |  |  | 126
02-06-00055 | 2003087/001 |  |  |  |  | 60
02-06-00056 | 2003087/002 |  |  |  |  | 60
BATTERY
02-06-00057 | 60 AMP |  |  |  |  | 6000
02-06-00058 | 90 AMP |  |  |  |  | 1000
02-06-00059 | 135 AMP |  |  |  |  | 1700
02-06-00060 | 540 AMP |  |  |  |  | 400
02-06-00061 | 530 AMP |  |  |  |  | 70
02-06-00062 | 30 |  |  |  |  | 700
02-06-00063 | 200 |  |  |  |  | 800
complete box battery Type:- 24 DRH 7
serial no. :- A9050158 F.O
capacity:- 511 A/AT 5 hour rate
volt:- 48
size:- 52x53x80 cm
each box have 12 battery
each battery size 50x14x11 cm
Equipment: kitchen equipment
Site: saddam medical city
02-06-00064 | Steam heated boiling pan adjustable boil dimension approx. 1X1x1 m capacity 200liter materials inner lining of acid poof s/s accessories mixer unit for hot and cold water strainers and removable baskets |  |  |  |  | 100
02-06-00065 | Equipment : KIMADIA COMPUTER SYSTEM
THIS SYSTEM IS DESIGNED AS THE FIRST STAGE SOLUTION FOR
COMPUTERISING THE STOCK MOVEMENTS OF MEDICAL ITEMS IN THE
MINISTRY OF HEALTH WAREHOUSES.THIS INCLUDES ALSO ALL THE
RELATED ACTIVITIES PRIOR TO IT,SUCH AS TENDERS, CONTRACTS, ETC, AND
OTHER ACTIVITIES RESULTING FROM STOCK ,SUCH AS QUOTA
SYSTEM, ACCOUNTING, AND FOLLOW UP OF ITS DISTRIBUTION (FROM THE
SUPPLIERS DOWN TO ITS DISTRIBUTION TO THE FINAL OUTLET).
THE SYSTEM CHOSEN IS NOT BY ALL MEANS THE LATEST STATE OF THE
ART TECHNOLOCHY,BUT ITS A SYSTEM ACCEPTABLE TO UN, SUITABLE FOR
ESTABLISHING THE STRUCTURE OF MORE, ADVANCED SYSTEM AS CHEAPLY
AS POSSIBLE ,AND SIMPLE ENOUGH TO BE TRANSFERRED AT LATER
STAGES TO MORE ADVANCED COMPUTER SYSTEM,BECUASE IT WILL BE
DESIGNED TO BE PORTABLE,
THE SYSTEM CONSISTS OF COMPUTER NODES IN EACH OF THE 13
WAREHOUSES AND EACH NODE WILL HAVE LOCAL PROCESSING
CAPABILITIES TO RECEIVE ,STORE,DISPACH MEDICAL SUPPLIES IN
ACCORDANCE WITH THE PROCEDURE LAIDED DOWN BY- MOU.
ALL NODES WILL BE CONNECTED IN THE SECOND STAGE. WITH THE
KAMADIA COMPUTER CENTRE IN THE MINISTRY OF HEALTH'
THE FOLLOWING HARDWARES AND SOFTWARES ARE REQUIRED
A- NETSERVER QUANTITY -14 UNITS
SPECS AS FOLLOWS
1-UPTO 16 GB INTERNAL STORAGE
2-SIX EXPANSION SLOTS-TWO PCI,TWO PCI/ISA,TWO ISA
3-RAM UP TO 198MB AND TWO UNITS WITH RAM 384MB
4-BUILT IN ASR
5- CD-ROM
6-PRE CONFIGURED NETWORK CARD
7-NOT LESS THAN 200 MHz PROCESSOR
8-TAPE BACKUPSYSTEM NOT LESS THEN 8 GBNATIVE STORAGE
9-EXTERNAL STORGE CABINET WITH 4.3 GB DRIVE
10- ORGALE DATA BASE LICEINCE FOR 16 USER ON EACH SERVER
11-UNIX OPERATING SYSTEM
ANY SYSTEM WITH ABOVE SPECS WILL BE ACCEPTABLE.
THE MACHINES MUST BE FROM BRAND SUPPLIERS
B-PC QUANTITY 130 UNITS
WITH THE FOLLOWING SPECS.
200 MHz PROCESSOR
16 MB RAM
1.6GB INTERNAL STORAGE
C- TERMINALS QUANTITY 130 TERMINALS
COMPATIBLE WITH THE MINI SERVER -ARABISED
D- PRINTERS QUANTITY 50 UNITS
E- LASER JET PRINTERS QUANTITY 50 UNITS
02-06-00066 | Special Equipment for directorate of protection & improvement environment
| Equipment:-Note book computer- |  |  |  |  | 10
-12.1 Active matrix display
- 200 MMX Intel Pentium processor
-512 Pipelined burst cache
- 32 MB EDO RAM
-2GB HDD (8ms)
-16X CD-ROM (removable)
- 1.44 3.5” Floppy disk drive
- 4 MB EDO PCI Graphics
- Zoomed video port ,video in jack
Infrared interface support
Arabic/ English key board
- 16 Bit built in sound W/Speakers
Integrated personal touched
- Two type II/ 0ne type III PCMCIA slot
- Rechargeable batteries (+2 Extra batteries)/ AC Adapter (220 V AC )/charger
Mobile care adapter
- Arabic windows 95 + MS plus! + MS office Professional with book shelf for windows 95, including original CD ’S & manuals
Deluxe carrying case
| - Hp Laser jet 6P printer with 10MB Memory + 10 extra toners |  |  |  |  | 6
| Multimedia projector with the following minimum specifications |  |  |  |  | 6
- 800 x600 SVGA
Power zoom focus
- 500 ANSI Lumens
video capable
Wireless PC mouse
recommended spare parts including Extra bulb
| PUS, APC back -UPS pro 1250 |  |  |  |  | 6
| Video camera with all accessories (VHS) |  |  |  |  | 50
| Television |  |  |  |  | 50
| Video with all accessories |  |  |  |  | 50
| Trans code |  |  |  |  | 50
| Recorder with all accessories |  |  |  |  | 50
| Photo camera |  |  |  |  | 50
| Over head projector |  |  |  |  | 50
| Slide projector with accessories |  |  |  |  | 50
02-06-00067 | MANUAL HYDROLIC JACK |  |  |  |  | 200
TYPE TROLLY JACK
CAPACITY : 1TON 0.250TON
02-06-00068 | MANUAL MECHAMICAL JACK (0.250TON)WITH SPARE PARTS FOR TWO YEARS |  |  |  |  | 200
TYPE TROLLY JACK
CAPACITY : 1TON 0.250TON
02-06-00069 | Passengers intercity staff bus 20 to 30 passengers,automatic doors ,diesel engine,air condtioned,apholestered chairs stainless steele fram,sliding glass windows with curtains,rubber mat floor, tinted windshield , stereo radio-recorder,ceiling hanging grips, |  |  |  |  | 1250
Equipment: kitchen equipment
Site:saddam medical city
02-06-00070 | Electric boiling pan, 3PH, 380 V, 50 HZ, and 20 KW, dimension: approx. 1X1X1 m , capacity : 100liter , material inner lining of acid proof S/S, outer casing and lid of S/S with foundation frame |  |  |  |  | 100
02-06-00071 | Electric boiling pan, 3PH, 380 V, 50 HZ, 30 KW, dimension approx. 1.25X1X1 m , capacity : 200liter , material inner lining of acid proof S/S, outer casing and lid of S/S with foundation frame |  |  |  |  | 60
02-06-00072 | Deep fat fryer – floor model , 3 phase , 380 V ,11.2 KW , dimension : 600X600X900 mm, capacity :oil volume ,2X15 liter, material : top surface , well heating elements and sides of S/S , with 2 baskets |  |  |  |  | 50
02-06-00073 | Deep fat fryer – floor model , 3 phase , 380 V ,11.2 KW , dimension : 600X600X900 mm, capacity :oil volume ,2X15 liter, material : top surface , well heating elements and sides of S/S , with 2 baskets |  |  |  |  | 50
02-06-00074 | Potato peeler mounted on astounds, 3 pH, .5 KW dimensions approx. 500X750X 1000mm capacity approx. 28 I Bs /load materials stand of cast iron cylinder of aluminum |  |  |  |  | 20
02-06-00075 | Meat bond saw , 3 pH , 1.5 HP dimension approx. 520 X600X1500mm capacity work table 520X 660mm table travel 300mm ,blade speed 22m/sec s/s table |  |  |  |  | 40
02-06-00076 | Vegetable mill , 3 pH 0.75 KW or 1 pH equivalent dimensions approx. 750X300X500mm capacity 5-10 kg /min material machine casing polyurethane and acetyl with all accessories |  |  |  |  | 35
02-06-00077 | Food cutter 3pH 380 V 50HZ dimensions approx. 750 X600X500mm capacity volume of bowl 11liter speed of bowel 16/33 rpm speed of knife 1400 /2800 rpm material bond of s/s cover and stand of elect of aluminum with all accessories knifes s/s spanners |  |  |  |  | 40
02-06-00078 | Heavy duty meat miner 380 V 50HZ 1.5 KW capacity approx. kg/hour 300, diameter of rotating knives 82 mm dimension approx. 400X470X 500 |  |  |  |  | 50
02-06-00079 | Universal kitchen machine 1 pH dimension space required 370X270X500mm material casing of light alloy accessories mixing attachment 20 liter bowel capacity meat miner with 3, |  |  |  |  | 40
4 ½ , 13mm cutting plates and one four bled knife mashing machine
02-06-00080 | Steam heated boiling pan adjustable boil dimension approx. 1X1x1 m capacity 200liter materials inner lining of acid poof s/s accessories mixer unit for hot and cold water strainers and removable baskets |  |  |  |  | 50
02-06-00081 | Equipment : Absorption chiller |  |  |  |  | 50
Site/saddam Medical city
capacity : 1000 RT
Replacement to 16 JE carrier
- Eva & Abuse :
copper tubes 22 BWG X 1/4” O.D
Eva. tubes have 19FPI
Abuse. tubes are prime surface
- Evaporator :
model 16 JE 707
in - out temp. (C O) : -12.5 - 7
flow ( L/S) :- 149
tube velocity (M/S) :- 1.79
pass no. :- 2
- Absorber :
model 16 JE 707
in temp .(C 0) :- 29.4
flow (L/S) :- 240
tube velocity (M/S): 1.87
pass no. : 2
con. & gen.
3/4 “ O.D
condenser tubes are plain 22BWG copper
generator tubes are 19 BWG Ca- Ni alloy 90-10
- con .
model 16 JE 707
out temp. (C0) :- 38
flow (L/S): - 240
tube velocity (M/S):- 3.28
pass no. : 1
gen.
Model 16 JE 707
Steam Pr - ( bar gauge ) :- 0.772
Steam rate ( G/SEC) :- 2275
02-06-00082 | Equipment : Centrifugal electrical chiller |  |  |  |  | 50
Site/saddam Medical city
Replacement to 17FA carrier
Capacity : 1000TR nominal.
Compressor : Hermetic motor - compressor
out put- 1000HP
Volt- 380 V , 3PH, 50 HZ
full automatic load control
full protection .
Evaporator: model 17 FA ZZ
in- out temp. ( Co): 7- 4.4
flow -(L/S) : 306
tube velocity ( M/S): 2.5
pass no. : 1
condenser: model FAZZ
in out temp. (Co) : 29.4- 35.5
flow ( L/S) : 170.3
tube velocity (M/S) : 2.6
pass no. : 2
tubes -tube length (m) : ZZBWG - 3.7
02-06-00083 | Equipment : Centrifugal electric chiller |  |  |  |  | 20
Site/saddam Medical city
Replacement to 17 DA carrier
capacity : 3000 TR nominal
Motor : out put : 2240 KW - 3000 HP
volt : 11000V , 3PH
RPM : 1488
AMP : 138
compressor : model 17 DA - 74
B.H.P : 2234.86 KW
drive H.P: 2240 KW
speed increase : 5439/ 1488
cooler: model 17 DA - 73-ZZ
tube length (m) : 6.7
flow (L/S) : 311.6
in out temp (Co) : 12.5 - 4.38
no. of tubes : 1410
condenser : model 17DA - 67
tube length (m) : 4.6
flow (L/S): 471.9
in out temp (Co) : 29.4- 35.9
no. of tubes : 1801
no. of tubes for economizer : 199
02-06-00084 | Equipment : air compressor with motor |  |  |  |  | 50
Site/saddam Medical city
pneumatic control
motor : 30 HP . 380 V , 3 pH , 50 HZ, 2300 L/min
max. discharge pressure : 20 bar
operating pressure : 12 bar
02-06-00085 | Equipment : air compressor with motor |  |  |  |  | 40
Site/saddam Medical city
diesel starting
motor : 2.6 KW , 3PH, 380V, 50HZ, 1500 rpm 0.065 m3/min 2.3 CFM
max working pressure: 3200 PSI,
02-06-00086 | Equipment : Incinerator |  |  |  |  | 700
pyloric incinerators without grate to ensure complete combustion to incinerator general hospital waste including paper , wrapping material , plastics, animal and vegetable waste and pathological waste. Incinerators must be capable to receive the above waste without separating
100 mg/nm3 .
content of CO: max. 0.002 %
visibility of flue gases : max. 1 ring element
the incineration must not produce any smell ( the post combustion temp. must be above 800 Co).
volume of ash : max. 3% of initial
volume
weight of ash: max. 12% of initial
weight
the waste must be completely burnt & the contact of unbent organic matter of the ash must not exceed 3% . suppliers must forward with the quotation a document by the natural official institution proving that the above standard are achieved . preference is given to incinerator achieving the above figures without additional filtration equipment .
capacity :100K/hr
Design : incinerator of the pyrolytic type are preferred . it should be able to operate the incinerator as follows:
manual feeding through special feeding door with temp. lock in order to protect from accident .incinerator must be without grate in order to avoid liquid waste to fall into the ash container without being incinerated .
incinerator must be equipped with primary and one secondary ( pilot ) burner . the fuel consumption of the burners is to be indicated in the offer .
control : automatic control with all necessary swishes , lamps , gauges , etc. in order to ensure automatic operation of the incinerator .
electrical supply : 220 - 380 V , 50 cycle
chimney : stainless steel chimney of sufficient length and diameter with spark arrest.
fuel oil tank :main storage fuel oil tank made from steel plate , sand plastid and provided with protecting paint,
capacity : 10000lt and daily fuel tank 1000lt
spare part : itemized and priced spare parts list sufficient for five years.
training: for tow engineer and tow technetium in your factory for the period of three week.
02-06-00087 | Equipment : kerosene refrigerator |  |  |  |  | 700
refrigerator work with electric heater & kerosene
- size 12 ft3
dial thermometer on the door
- refrigerator have tow door first for freezer & the second for refrigerator .
02-06-00088 | Equipment : meat cold store |  |  |  |  | 1000
walk in freezers to preserve fresh meat at internal temp. ranging from (-15 C) to (- 25) at the following ambient conditions :
summer : DBT 50 Co
WBT 25 Co
winter : DBT 1 Co
WBT - 2 Co
Internal volume of freezer : not less than 20 M3
A : CONSTRUCTION :
1- freezers shall be shipped in knock - down section easy to re- effect .
2- cabinet interior shall be made of heavy corrosion - proof aluminum - floor made of heavy gauge anti- slip aluminum ( Sequa plate) .
3- cabinet exterior shall be made of aluminum coated with a white weather - proof coating to make it suitable for out- door installation .
4- insulation shall be sufficient to maintain the specified internal temp. in the specified ambient conditions but shall be not less than 12 CMS of polyurethane .
5- door shall be constructed of aluminium andshall have an external lock with keys . Door handle can be operated from inside and outside low voltage heater wire strip with electrical control shall ne provided apush - button shall be fitted inside to sound an alarm in case a person is trapped inside .
6- shelves and hangers shall be made of strong rust - proof materials . Shelves shall be grid type thre quarters of the space shall be pccupied by she lves the rest by hangers .
7- Light weigh shade to protect the cabinet from rain and sun to be fitted or top of it shape size and material of shade shall be suggested by tenderer
8- dial thermometer
9- audio and visual alarm for high temp .
10- sufficient interaal lighting automatically switdes on when door opens
11- air cur ain the door operates automatically when door opens
B- REFRIGERATION SYSTEM
two inde pendent refrigration systems (each system having acompresor not less than 3 KW ) shall be installed each being capable to maintain the required internal temperature at the specified ambient conditions an automatic alternator aclock timer shall be furaished to aotamatically reverse the sequence of operation of the tow systems to assure even wear- should one sysstem be unable for any reason to maintain the required temperature the second sysstem shall automatically cut - in and together sysstem shall automatically cut- in and together both sysstem shall bring the temperature down to the required level . visual indication of the operation and faults of the sysstems shall be shown on the control panel capacity and type of compressors used shall be mentioned in the offer . the entire sysstem shall utilize heavy - duty refrigeration copper tuibing no aluminium or steel tubing shall be used . evaporator fins shall be anti - corrosion type - automatic electrical defrost with pipe for drain valve shall be
C: ELECTRICAL SYSSTEM
sysstem shall operate from single - phase , 220V . 50HZ supply - or from three - phase 4 - wire 380/220V .
D-SPARE PARTS:
an itemized and pricid spare - parts list sufficient for five years repair and maintenance of the equipment shall be submitted with the offer . the peace shall be C&F baghdad and the spares shall be shipped with the freezers . Among other things , the list shall include the fol;owing items:-
1-compressors
2-evaporator motor fan
3-blades for evaporator fan
4-condenser motor fan
5-blades for condenser fan
6-thermometer
7-thermostat & alarm thermostat
8-high/low pressure - cut out
9-oil pressure - cut out
10-door gasket with heater
11-contactor for compressors
12-relays & electrical switches & klix on
13-deforst heaters
14-automatic electric defrost
15-automatic alternator for reverse seguence
16-internal light bulb
17-over load
18-expansion valve
19-filter dir/ers
20-fuses of different ratings
21-solenoid valve
22-micro switch & spare for air curtain
23-alarm horn
TESTING , INSTALLATION AND GUARANTEE
A : TESTING AND GUARANTEE
tenderer shall guarantee and maintain the freezers for a period of tow years starting from date of putting them in operation . All equipment shall be tested and autstanding technicalproblms shall be discussed and settled in the firm prior to the shipment of the equi[ment and in the presence of our engineer . tenderershall pay for the return air tickets of our engineer and bear all costs of his stay with the firm including full - board lodging for a period of two weeks .
B: TRAINING :
tenderer shall train two persons on the repair and maintenance of the equipment , each person for a period of one month in his firm tenderer shall bear all eosts including return air - fair , full - board loding and any other expenses .
C : INSTALLATION :
tenderer shall make complete installation of all cold stores and freezers except civil works such as concrete base - all materials any offer not including complete installation shall be rejected .
NOTES
1-fresh meats shall be brough in stores at around 35 0C .
2-quantity of stored meats in each store is about 1500 KG .
3-load calculations shall be sent with the offer
02-06-00089 | EQUIPMENT: SUB – STATION |  |  |  |  | 2500 METERS
SITE: SADDAM MEDICAL CITY
BUSWAYS, 1600 AMP. RATING .
AS ABOVE BUT BETWEEN MV MAIN SWITCH BORD NAD TO 9-CHILLERS EACH 1500 AMP. FLC
02-06-00090 | submersible pump for spring well bore_hole pump=120meter head flow =7L/sec multi stage submersible pump = 380V 3PH 50HZ with spare parts for 5years |  |  |  |  | 20
02-06-00091 | Computer & Communication system to cover KIMADIA central, Doha, and sector warehouses. with high specs, UPS s, printers and universal bar code readers. |  |  |  |  | 15
02-06-00092 | Mechanical Governor control |  |  |  |  | 20
02-06-00093 | Water pump |  |  |  |  | 25
02-06-00094 | cooling tower |  |  |  |  | 75
company: CLIME CHAPPEE
Type :- (old) D31 E
Capacity :- 1.017 KW wet bulb :26 c
1-180.00 Kcal/hr water temp:- 38/30.8 c
Flow rate :-165 m3 /hr pressure drop :-2.5 m WG
Complete cooling tower :-
Which is same capacity at above and must be with separate motor for each blower and will work in high humidity weather 60% humidity and total hardness is for water 500 PPM recommended spare for 5 years include complete motor :-
Fins
Belt
Shaft
Spray nozzle
Bearing
Blower
Nozzle
Motor complete
Ball float valve
02-06-00095 | H.T. System |  |  |  |  | 100
We need to supply of eight H.T breaker with the specification below for each H.T breaker :-
Connections
It received power from (SOE) through two feeders one is operating and the other is standby and both are connected to the third H.T . breaker which satisfied the protection above and called general protection which supply the voltage to other five H.T breaker (3 for three transformer for hospital ; one for doctor residence ;one aspire)
All the H.T. breaker connected to earth switch individually in case of maintenance.
 We need
Recommended spare part incdudring 2H.T breaker complete and tools for repairing and maintenance complete maintenance operation and installation catalog and training for 2 engineer the system complete with the dimensions below length 3meter ; depth 1.7 meter ; high 2.25m
Notes:-
The system must be operated with vacuum method
Quantity :-
6 system for 6 site + Recommended spare
Old system
Original system with the specification below :-
CEM company (France)
Type MF- 120620
3ph 12kv 630A 50HZ
350 MVA
Motorized 110VD.C controlled voltage 110VD.C
Gas SF6 pressure 5bar
02-06-00096 | SHORT LIST FOR MATERIALS FOR CENTER OF NEUROLOGY (EQUIPMENTS AND SPARE PARTS AND ALL ACCESSORIES ) |  |  |  |  | 50
| Materials for mechanical works |  |  |  |  | Including refrigerant gas
Centrifugal or reciprocating water chiller 230 ton
02-06-00097 | A.H.U W/accessories |  |  |  |  | 70
02-06-00098 | Condenser Evaporate and Boiler pumps |  |  |  |  | 70
02-06-00099 | Heap filter(60 x60cm)for O.R |  |  |  |  | 1000
02-06-00100 | Perforated diffusers for O.R |  |  |  |  | 50 4-3x3m &5 -3.2x3.2m
02-06-00101 | El.Bd. W/temp and humidity sensors for O.R |  |  |  |  | 50
02-06-00102 | MATERIALS FOR SANITARY WORKS |  |  |  |  | 20Lot
Central medical gases system
02-06-00103 | Stainless steel scrub-up basins |  |  |  |  | 40 W/accessories
02-06-00104 | Oxygen plant |  |  |  |  | 20ot
02-06-00105 | MATERIALS FOR ELECTRICAL WORKS |  |  |  | Nurse call system | 20 lot 13n.st W/accessories
02-06-00106 | Bed head unit |  |  |  |  | 700Different types
02-06-00107 | Fire alarm system |  |  |  |  | 50ot Sys. W/accessories for 12 zones
02-06-00108 | Central clock system for O.R |  |  |  |  | lot 5 -master plus 10 -slave
02-06-00109 | Generator set (800 KVA) |  |  |  |  | 20
02-06-00110 | Bed passenger lift |  |  |  |  | 20
02-06-00111 | Sound reinforcement system |  |  |  |  | 20 Lot
02-06-00112 | Emergency exit light |  |  |  |  | 100
02-06-00113 | UPS system |  |  |  |  | 40 3-5kw plus 3-7kw
02-06-00114 | Sparkles switch socket |  |  |  |  | 300 Different capacities
02-06-00115 | Materials for civil works |  | Conductive PVC tiles for O.R dept |  |  | 540m^2W/accessories and adhesives
02-06-00116 | Ceiling panels for O.R |  |  |  |  | 210M^ 2 W/accessories and hangers
02-06-00117 | Wall panels for O.R |  |  |  |  | 560M^2 W/ accessories and built in items
02-06-00118 | PVC skirting for O.R dept |  |  |  |  | 5002M W/accessories and adhesives
02-06-00119 | Equipment : pumps |  |  |  |  | 100
Company name : Guinard France
Description
-Complete pump+motor (NE 6x16)
Q=100 m3/hr H=30-23
Kw 15 3ph , 400V
COs Q 0.89 r.i.p. = 2995
02-06-00120 | -set of repining kit for the pump (NE 6 x16) |  |  |  |  | 100
02-06-00121 | Complete pump + motor (NE3 x16) |  |  |  |  | 100
Q= 15 m3/hr H=30m
3ph COs Q 0.9, r.p.m=2850 400V
02-06-00122 | -Set of repining kit for the pump (NE 3x16) |  |  |  |  | 100
02-06-00123 | Accessories |  |  |  |  | 100
Microtck scanner A3 size (color)
02-06-00124 | Printer HP Desk jet 890C |  |  |  |  | 100
02-06-00125 | Digital Camera (Sony) |  |  |  |  | 100
02-06-00126 | Video in card (MPWGENCODER) |  |  |  |  | 100
02-06-00127 | Plotter A0 size (Disk jet color) |  |  |  |  | 100
02-06-00128 | Multi Media Projector |  |  |  |  | 100
02-06-00129 | Jackboot (20 CD changer) for Libra |  |  |  |  | 100
02-06-00130 | Copy Machines |  |  |  |  | 100
Minolta photocopy machine 2080
02-06-00131 | Kiss graph machine copy speed (60-130 copy per minute) GR-1750 or GR-3750 |  |  |  |  | 100
02-06-00132 | Video and calling system requirement |  |  |  |  | 200
Video camera digital with motorized connected to the current system
02-06-00133 | 27” Monitor video in –video out connected to the current video system |  |  |  |  | 200
02-06-00134 | Amplifier for current audio calling system |  |  |  |  | 100
02-06-00135 | Video recorder U-Match |  |  |  |  | 100
02-06-00136 | Video Recorder VHS |  |  |  |  | 100
02-06-00137 | Video Caddie U-Match |  |  |  |  | 2000
02-06-00138 | Video Caste VHS |  |  |  |  | 500
02-06-00139 | Equipment:-Pegging system |  |  |  |  | 100
-Complete Paging system with its control station and 5 watt transmitter and 100 radio receivers.
the system either independent or interfacing with telephone exchange type.
Model:- cite allocate v-2505 medium capacity epabx (64x320) cabinet reference 0A075080101 (A20750044/E)
Program reference FAH 04H 10H 03H
supply Complete maintenance and operating installation catalog and spare part catalog
training of our staff in maintenance factory
-spare part for 5 year
02-06-00140 | Equipment:- water softener |  |  |  |  | 75
Description
-supply complete water softener with the values and all accessories instead of old model:-
SF602 CSB meter controlled fully automatic.
Capacity:- 9000/m3
Maxflowrate:- 10 m3/huh
Hardness of treated water 0.TH
Pressure drop:- 80 KPA (8MWG)
Voltage:_220V/50HZ
Operating pressure between (2 and 6 bar) 2 and 6 KPA/cm
Salt capacity:-400 KG
Reagent tank:- 120L
Company name:-EAU ET IN DUSTRE
-supply test kit for testing water with reagent 12 set
supply Complete maintenance and operating and installation catalog and spare part catalog
give list of Spare part for 5 years
training of our staff in manufacture factory
02-06-00141 | Equipment:- Package unit package complete which supply cool air directly by duct to the building |  |  |  |  | 2000
Capacity:- 10TON
380 V 50HZ ,3PH,R22
Ambient temp. :- 60 C
Linseed temp.::- 12 C
Training 3 engineer for 2 weak spare part for 5 years
02-06-00142 | petium 333MHZ MMX (INTEL) COMPLIENT WITH YEAR 2000 (XION) |  |  |  |  | 100
MINITOWER CASE
64MB RAM (512CACHE)
UP TO 5GB HDD
15” SVGA MONITOR WITH 8MBAGP CARD (SVGA)
144 FDD (3.5)”
104 AIL KEYBOARD +(MOUSE &PAD)
MULTI MEDIA KIT (32X CD-ROM+ 16-SOUND BLASTER+SPEACERS+microphone)
CD-WRITER 2X2X6
FAX –MODEM CARD
LAN CARD 32 BIT (PCI)
WITH 1.4 APC UPS
TYPE 2
PETIUM 333MHZ MMX (INTEL) COMPLIENT WITH YEAR 2000 (XION)
MINITOWER CASE
32 MB RAM
3 GB HDD
14”SVGA MONITOR WITH 4MB AGP SVGA CARD
1.44 FDD (3.5)”
104 AIL KEYBOARD + (MOUSE&PAD)
CD-ROM 32X SPEED
LAN CARD 32BIT (PCI)
WITH 1.4 APC UPS
TYPE 3
PETIUM 300MHZ MMX (INTEL) COMPLIENT WITH YEAR 2000 (CELERON)
MINITOWER CASE
16MB RAM
UP TO 2GBMDD
14” SVGA MONITOR WITH 2MB SVGA CARD
1.44 FDD 3.5”
104AIL KEYBOARD + (MOUSE & PAD)
LAN CARD 32 BIT (PCI)
CD- ROM 24X SPEED
WITH 1.4 APC UPS
PRINTERS
EPSON LQ 2170 DOTMATRIX WITH ARABIC
HP LASER GET 6P
SCANNER
AT LEAST 4800 DPI FLAT BED PAGE SCANNER
mother board intel corporation with cpu
bios american megatrend inc (AMI)
ram memory micronics . Or kingston technolgy corp
hard disk seagate technology inc . Or western digital corb
monitor sony electronics inc.or samsong electronics america
floppy disk drive teak america inc.or mewlett packard
keyboard & mouse microsoft corp
multimedia kit creative labs
CD-rim panasonic communications& system co
fax-modem card hayes micro computer products inc
Equipment:fan coil unit
COMPANY NAME: wesper
02-06-00143 | COMPLETE FAN COIL TYPE V.P.N 61 SINGLE SHAFT |  |  |  |  | 1200
02-06-00144 | COMPLETE FAN COIL TYPE V.P.N 81 DOBLE SHAFT |  |  |  |  | 660
02-06-00145 | COMPLETE FAN COIL TYPE V.A.C 41 SINGLE SHAFT |  |  |  |  | 75
02-06-00146 | COMPLETE FAN COIL TYPE V.A.C 81 DOBLE SHAFT |  |  |  |  | 55
02-06-00147 | COMPLETE FAN COIL TYPE V.A.C 111 DOBLE SHAFT |  |  |  |  | 55
SPARE PART FOR 5 YEARS INCLUDING THER MOSTAT MOTOR SELECTOR SWITCH
catallog for the spare parts, models ,maintenance and operation
TRAINING for our STAFF engineers
02-06-00148 | EQUIPMENT CHILLER |  |  |  |  | 250
CAPACITY : 550
CENTRIFYAL TYPE WATER COOLED
SPARE PART FOR 5 YEARS
TRAINING FOR ENGINEAR
SUPPLY OPERATION AND MAINTENANA
CATOLOG WITH SPARE PART LIST
INSTALLATION AND OPERATION AND MAINTEANCE FOR ONE YEAR..
02-06-00149 | WATER COOLER COMPLATE WITH |  |  |  |  | 10000
¼ OR 1/3 HP COMPRESSON 50HZ SINGLE PHASE 220V
SYEARS SPARE PART
TRAINING FOR ENGINEER AND TECH
02-06-00150 | Equipment :- Window unit |  |  |  |  | 25000
Air condition with heater
Capacity :- 1.5 ton
220 v , 50 Hz , 1 pH
hotel cooled , R22
spare part for 5 years
Training for our tech.
02-06-00151 | Equipment :- split unit |  |  |  |  | 10000
Split unit with heater
Capacity :- 3 ton
220 V , 50 Hz , 1 pH
hot and cooled R22
spare part for 5 years
training for our tech
02-06-00152 | Equipment :- deep freeze |  |  |  |  | 1000
Deep freeze complete unit flat type inside temp. required :- 40 Co , size: 500 LT
220V , single, phase 1 , 50 HZ
spare part for 5 years
training for engineer and tech
Supply catalog spare part and operation and maintenance
02-06-00153 | Equipment :- chiller Air cooled |  |  |  |  | 700
Capacity :- 80 ton
Ambient temp :55Cْ
Water inlet : 6 Cْ
Water outlet : 12 Cْ
Compressor type : Semi hermetic
coil material copper tube with aleminuim fins
fan type propeller
evaporator sheel and tubs
(cooler type) pumps flow rate suitable for the chiller
air handling units with suitable capacity
electrical board for operation (pumps ,chiller , air handling units)
02-06-00154 | Equipment:- cooling tower |  |  |  |  | 80
Complete cooling tower
Capacity : 4 .201.200 Kcal/h
Working weather 60% humidity and 500 PPM total hardness for water
Water flow : 7800 L/min
Water in :- 41Cْ
Water out :- 32 C ْ
Spare part for 5 years
Training for engineer and tech
Supply catalog for operation and maintenance and spare part list.
02-06-00155 | Equipment:- cooling tower |  |  |  |  | 60
Capacity :80 ton
Water temp. 38/ 30 Cْ
Complete cooling tower must be separate motor for each blower and will work in high
Humidity weather 60 % Humidity and total hardness is for water 500ppm
Recommended spare for 5 years.
Include complete motor
Fin , belt,shaft, spray nozzle , bearing , blower ,
Nozzle , motor complete, ball float valve
Training for engineer and tech.
Complete catalog for spare part and operation maintenance catalog
02-06-00156 | Minibus 21 Setae, Two Wheel Drive with four doors with Air Conditioner, Petrol engine with service, operation, spare parts manuals in English and service and Fast moving spare parts for 2 years operation |  |  |  |  | 1for the North
02-06-00157 | Fuel Tanker Scan, Complete Set, 9 cube metros (m3) spare part with service, operation, spare parts manuals in English and service and fast moving spare parts for 2 years operation (other alternative Volvo or Mercedes) |  |  |  |  | 3 for the North
02-06-00158 | SPECIFICATIONS FOR BLOOD REFRIGERATOR CARS |  |  |  |  | 300
BIAS VEHICLE
_ ENGINE:(4-6) CYLINDER
PETROL ENGINE
WATER COOLED
CAPACITY 2600CC AND MORE
TRANSMISSION: MANUAL GEAR BOX 4- SPEED WITH ONE REVERSE FLOOR SHIFT
DRIVE : FOUR WHEEL DRIVE THE REAI AXLE EGUPED IN EACH SIDE DOUBLE WHEEL
BRAKE: DRUM BRAKE IN EACH WHEEL WITH BOOSTER ASSIST BARKING BRAKE TO BE CONTROLLED BY HAND GETTING ON THE REAR WHEELS
- STEERING: POWER STEERING LEFT HAND DRIVE
- SUSPENSION: HEAVY DUTY LEAF SPRING IN EACH REAR AND FRONT WHEELS
- GAUGES: ALL IN METEORIC SYSTEM .
- AIR CONDITION AND HEATING: TO BE SUPPLIED FOR DRIVER CAB
- CAB: DOUBLE CABIN
FRAME AND CLASSIS :- TWO PARRELL CHANEL CLASSIS
- ELECTRIC EQUIPMENT: HEAVY DUTY 12 VOLT 75 AMP /H BATTERY
ANTENNA
INSTALLATION OF RADIO ANTENNA IN EACH AMBULANCE AT THE ROOF.
WIRELESS EQUIPMENT: EACH AMBULANCE EQUIPPED WITH RADIO (WIRELESS COMMUNICATION DEVICE).
- LOAD CAPACITY: THE VEHICLE CAN CARRY NET WEIGHT NOT LESS THAN 1000 KG
- SIREN AND BEACON: THE CAR EQUIPPED BY BEACON LONGITUDINAL IN UPPER FRONT OF THE CAR AND EQUIPPED BY DEVICE FOR COMMUNICATION
- ASSESSORS: JACK AND HANDLE, WHEEL RING, HAZARD TRIANGLE
- SPARE TYER ( DOUBLE TYER )
TWO GENERATORS SET TO BE AVAILABLE EACH ON CAPABLE TO OBERATE CONTINOUSLY FOR SIX HOURS
CAPABILITY OF CONNECTING REFRIGERATOR AND FREEZER WITH EXTERNAL ELECTRICAL SOURCE INCLOUDING ( CABLE 100M LENGTH WITH THREE OUT LET AND ANOTHER ELECTRIC Accessories AVAILIBLE ALL THE TIME IN THE CAR )
BLOOD BOX COMPARTMENT
THE BOX WILL BE ENOUGH TO CARRY THE FOLLOWING:
- TWO BLOOD REFRIGERATOR (VERTICAL TYPE) EACH CAN CARRY 100 UNIT OF BLOOD BAG
- TWO DEEP FREEZER (VERTICAL TYPE) EACH CAN CARRY 150 UNIT OF BLOOD DERIVATIVES
INSIDE TEMP FOR REFRIGERATOR + 2C TO +6C
INSIDE TEMP FOR DEEP FREEZE -30 TO -60C
- AMBIENT TEMP:60C
AUDIO and VISUAL for LIGHT TEMP and LOW TEMP MUST BE FITTED in EACH refrigerator and FREEZE and WILL BE SHOWN ALSO in DRIVE CAB
DALE THERMOMETER MUST BE PROVIDED ON THE REFRIGATOR AND FREEZ AND WILL BE SHOWN ALSO IN DRIVER CAB
DAY RECORDER ON EACH REFRIGATOR AND FREEZ
EACH refrigerator and FREEZE have TWO SEPARATING COMPRESSOR (ONE work and ANTHER STAND BY )
- EACH REFRIGERATOR AND FREEZE HAVE STAINLESS STEEL STEAD DOOR (NOT GLASS)
- AUTOMATIC DEFORESTING FOR EACH REFRIGERATOR AND FREEZE AND THE DRAIN WATER WILL BE THROWN OUTSIDE THE CAR
- THE REFRIGERATOR AND FREEZER WILL HAVE REMOVABLE DRAWER
- REF. GAS: R12 OR, RR22 OR R502
- TOW MINI COOLING BOXES FOR MANUAL TRANSPORTING THE BLOOD BAGS
- THE GENERAL BOX ARE SUITABLE FOR THE JOB OF THE OPERATION OF BLOOD CARRYING IN EACH ITEM .AND EQUIPPED BY TWO REAR DOOR OPERABLE TO THE SIDE
RECOMMENDED SPARE PARTS FOR 5 YEARS
TRINING FOR TOW ENG. TOW WEEKS AND ONE DOCTOR(physican) FROM BLOOD BANK FOR TWO WEEKS
02-06-00159 | Equipment Gas Boiler |  |  |  |  | 200
Supply complete unit with its all accessories instead of old model conic flexiflame 70 cp. Gases serial No. 82487612-20
Company name :- CHAFFOTANUX ETMAURY
- give list of spare part for serer
- supply complete maintenance and operating and installation and spare part scatalog
- Training of our staff in manufacture factory
02-06-00160 | Centralized cooker s |  |  |  |  | 100
02-06-00161 | Bata peeling machine |  |  |  |  | 100
02-06-00162 | Tomato press |  |  |  |  | 100
02-06-00163 | Horizontal Deep freeze 16” foot |  |  |  |  | 100
02-06-00164 | Washing machine laundry |  |  |  |  | 100
02-06-00165 | Press |  |  |  |  | 100
02-06-00166 | Betts for Iron roller |  |  |  |  | 500
02-06-00167 | Pentium 2 Intel |  |  |  |  | 800
02-06-00168 | CPU 333 MHz with cache RAM 128 MB |  |  |  |  | 800
02-06-00169 | Hard disk 9 GB |  |  |  |  | 800
02-06-00170 | SVGA card 4 MBV RAM |  |  |  |  | 800
02-06-00171 | 17” color SVGA monitor |  |  |  |  | 800
02-06-00172 | Screen filter |  |  |  |  | 800
02-06-00173 | LAN card 32 Bits |  |  |  |  | 800
02-06-00174 | CD –Drive 34 X |  |  |  |  | 800
02-06-00175 | Sound D32 Bit 3 D |  |  |  |  | 800
02-06-00176 | HP laser jet printer 6p++10 extra toner |  |  |  |  | 800
02-06-00177 | Modem Fax card (56.6) KBPS |  |  |  |  | 800
02-06-00178 | English/Arabic KB (104 Keys) |  |  |  |  | 800
02-06-00179 | MS mouse |  |  |  |  | 800
02-06-00180 | Mouse –Peed |  |  |  |  | 800
02-06-00181 | 3.5 FDD HD |  |  |  |  | 800
02-06-00182 | HP Laser jet printer |  |  |  |  | 800
02-06-00183 | Extra Black Toner |  |  |  |  | 1000
02-06-00184 | FORK LIFT (5 TON) |  |  |  |  | 200
1. DIESEL ENGINE 4 CYLINDER WATER COOLED
2. BATTERY 12V
3. NORMAL HYDRAULIC GEAR
4. MAX HEIGHT 3.5M
PACKAGE UNIT (AIR COOLED) SCHEDULE
Cod | No. Req | Summer |  |  |  |  | Winter |  |  | blower
|  | Cooling load kcal/H |  | Evaporate temp C |  |  |  | Electrical heater |  | Fresh air (m/h) | Kw
| Qty | Effective sensible load | Total load | Entering |  | Leaving |  | Kw | No.of stage
|  |  |  | D.B | W.B | D.B | W.B
02-06-00185 | 50 | 65700 | 98400 | 28 | 17.5 | 14 | 9.5 | 70 | 2 | 4980 | 46
02-06-00186 | 50 | 55200 | 81900 | 33 | 19.8 | 143 | 9.5 | 58 | 2 | 4400 | 37
02-06-00187 | 50 | 19400 | 28200 | 28.4 | 17.5 | 14 | 9.5 | 20 | 2 | 1630 | 13.6
02-06-00188 | 50 | 29670 | 44100 | 28.4 | 17.5 | 14 | 9.5 | 31 | 2 | 2550 | 22.8
02-06-00189 | 50 | 12510 | 18150 | 28.4 | 17.5 | 14 | 9.5 | 12.8 | 2 | 1020 | 8.9
02-06-00190 | 50 | 41000 | 50500 | 28.4 | 17.5 | 14 | 9.5 | 36 | 2 | 2720 | 22.6
02-06-00191 | 50 | 12510 | 18000 | 28.4 | 17.5 | 14 | 9.5 | 12.7 | 2 | 1020 | 8.9
02-06-00192 | Size of clinker /1st stage 406. 4mm (16”) tow |  |  |  |  | 50set
02-06-00193 | Z ND stage :288 .6mm (9)” tow |  |  |  |  | 50set
- Power transmission / direct coupling
- The compressor used to produce medical oxygen Gas under normal condition
- Compressor manufacturer / IHI ishikawajima – industries Co. It’d Tokyo Japan
Head office e : New ohtemavhi Bldg. 2- chime . 2chlemachi
Chiyoda .KU Toko. Japan
Tel Toko (03) 244.6496)
Telex J22232 (Chico j 22232)
J 22490 , JJ2439Cabla address : Iho Toko
- Installed & Commissioning by:
Toko Bussan Co. Lt.
Twix 242- 2914
Fax 03-423 – 4821
02-06-00194 | Teflon Pistonring 2nd Stacie cood No. E238201 |  |  |  |  | 100
02-06-00195 | Teflon Piston ring ist stage cood No. E148201 |  |  |  |  | 150
02-06-00196 | Bull Ring 2nd Stage cood No. E238202 |  |  |  |  | 100
02-06-00197 | Piston Assy Ist stage cood No. E141600 |  |  |  |  | 60
02-06-00198 | Discharge valve seat |  |  |  |  | 900pcs
02-06-00199 | inlet valve seat |  |  |  |  | 900
02-06-00200 | I- Typethermometer (0-100C) |  |  |  |  | 50
02-06-00201 | L- Type Thermometer (0-200C) |  |  |  |  | 300
02-06-00202 | THRENAY SOLENOIO VALVE |  |  |  |  | 300
02-06-00203 | Oil preserve |  |  |  |  | 300
02-06-00204 | Chain over suttee |  |  |  |  | 300
02-06-00205 | AIR Pressure switch cood No. G319968 |  |  |  |  | 300
02-06-00206 | Temperature switches (120-215C) cood no. G631301 |  |  |  |  | 300
02-06-00207 | Crank shat Assy cood No. D266700 |  |  |  |  | 300
02-06-00208 | Oilier PIN cood No. |  |  |  |  | 300
02-06-00209 | Retaining Ring cood No. D26706 |  |  |  |  | 300
02-06-00210 | Bearin6 collar cood No. D260707 |  |  |  |  | 300
02-06-00211 | Bearing Coeur cood No. D260708 |  |  |  |  | 300
02-06-00212 | Collar cood No. D260709 Flintier |  |  |  |  | 300
02-06-00213 | Filigree cood no. D260710 |  |  |  |  | 300
02-06-00214 | Bolt cood no. D110711 |  |  |  |  | 300
02-06-00215 | Key cood No. D260712 |  |  |  |  | 300
02-06-00216 | Oilier sleeve cood no. D260713 |  |  |  |  | 300
02-06-00217 | Bearing cood No. 0.0260714 |  |  |  |  | 300
02-06-00218 | Bearing cood No. D260715 |  |  |  |  | 300
02-06-00219 | Connecting Rods cood No. D111400 |  |  |  |  | 300
02-06-00220 | Ding end Bolt cood No. D111403 |  |  |  |  | 300
02-06-00221 | Caste Nut Cood No. D111404 |  |  |  |  | 300
02-06-00222 | Crank pin Bearing Cood. No. D111406 |  |  |  |  | 300
02-06-00223 | Wrist P/N Metal cood No. D111407 |  |  |  |  | 300
02-06-00224 | Cloture P/N cood No. D961814 |  |  |  |  | 300
02-06-00225 | Cross Head Assy Cood No. D111300 |  |  |  |  | 300
02-06-00226 | Wrist P/N covers cood No. D111 303 |  |  |  |  | 300
02-06-00227 | Wrist P/N D111304 |  |  |  |  | 300
02-06-00228 | Lockwasher Cood no. D111305 |  |  |  |  | 300
02-06-00229 | Bolt Cood No. 0430765 |  |  |  |  | 300
02-06-00230 | Destine Rod cood No. E121606 |  |  |  |  | 300
02-06-00231 | Precision control thick meter |  |  |  |  | 300
| 0-3005 Freq. 0-4000 |  |  |  |  | 300
02-06-00232 | Thermos couple for outlet and inlet Tem. |  |  |  |  | 300
02-06-00233 | Tem. Controller T 675A |  |  |  |  | 300
02-06-00234 | Ceramic filter |  |  |  |  | 300
02-06-00235 | Flexible hose for tank lorry |  |  |  |  | 300
02-06-00236 | Ball valve for pump (tank lorry) |  |  |  |  | 300
02-06-00237 | Pump Assy for tank lorry |  |  |  |  | 300
02-06-00238 | Flexible hose for filling station |  |  |  |  | 300
02-06-00239 | Complot O2 valve for oxygen cylinder type G11 |  |  |  |  | 300
Water pump
Manufacture: old type LEF1: any anther new model
Equipment to the following old pump good quietly
| Article |  |  |  | Qty of repair kit | Qty of complete pump
02-06-00240 | Contifagal pump with motor complete old model : B125/25 name Q forte (m3/h) ; 95 380volt, 50HZ, 3PH |  |  |  | 200 | 100
02-06-00241 | Centrifugal pump with motor complete old model :- B 125/20 N Q floweret 9m3/h0:160 |  |  |  | 200 | 100
Head:- 26m
volt 380 50hz 3ph
02-06-00242 | Centrifugal pump with motor complete old model :- B125/30 Q floweret m3/h : 182 Head:- 21m |  |  |  | 200 | 100
Volt:- 380 , 50Hz 3ph inletpipe inch :- 5 outlet pipeinch;-4
02-06-00243 | Centrifugal pump with motor complete old model :- B125/25 Q floweret m3/h:- 95 |  |  |  | 200 | 100 |  |  |  | 10
Head :- 17m
Volt 380, 50Hz,3Ph
02-06-00244 | Centrifugal pump with motor |  |  |  | 200 | 100
Old model :- B125/30( Hot water )
Q floweret (m3/h):- 99
Volt:- 380,50 Hz, 3ph
02-06-00245 | Centrifugal pump with motor old model :- B40132 |  |  |  | 200 | 100
R.P.M= 1450
Q floweret m3/h =14
Head ;- 25 volt;- 380 Hz = 50 pH: 3
02-06-00246 | Centrifugal pump with motor |  |  |  | 100 | 100
Old model :- B80 /35 Qflowrate :- m3/h 50 volt:- 380 , 50Hz,3ph
02-06-00247 | Centrifugal pump with motor old model :- B125/35 Q floweret (m3/h) :60 volt:- 380 50Hz, 3ph |  |  |  | 100 | 100
02-06-00248 | Centrifugal pump |  |  |  | 100 | 100
With motor old model :- bob 80/25 Q floweret m3/h :59 volt:- 380 , 50Hz,3ph
02-06-00249 | Electric sewage pump head :- 15-20
| 380volt: 50Hz,3ph supply complete maintceance and operating installation catalog and spare part Catalan training of our staff in maintenance factory |  |  |  | 150 | 100
02-06-00250 | Drying tumbler |  |  |  |  | 500
Capacity 15 Kg/load (dry weight ) 3 load /hour
Heating by electrical element
drum stainless steel 18/8 timer and thermo stat controlled inter lock stops cycle when door opened
connection to 380v 50hz 3ph
spare part list for 3 years
operation in stallation repair and spare parts manual with each drying tumbler
Training tow engineers for 3 weeks in the factory
02-06-00251 | Press |  |  |  |  | 400
Capacity 20 kg
Stainless steel inner for drum
Automatic operation pnognamebel
All accessories needed supply for prepare operation
Connection 380 V 50 HZ 3PH
List for spear part recommended 5 years
All document , menteenens , operation repair
Training tow engineers for 3 weeks in the factory
02-06-00252 | Steam dryer |  |  |  |  | 500
capcity 50kg dry /load with 3 load /hr
heating : steam (6-8) bar reverse rotation cylinder inter lock door for safty
timer control indication lamps and any other necessory components must be included
inlet and out let flexible steam pipes exheust flexible pipe 6m for each automatic start -stop starter ,steam trape sylinder material should be corrosion - proof itemized and speratly priced spare part list for 3 years
operation installation repaier and spare parts manual with each tumbler
connection to 380 V 50 HZ 3PH
02-06-00253 | iron steam |  |  |  |  | 400
steam heated press roller two meters long
variable speed lowering raising switch for reverse rotation
finger protection provided rotation left and right
steam heated at a pressure of (8-10 )bar
complete with exhaust fan and all internal electric wiring steam trap connection to 380v 50hz 3ph
spare part list for 3 years
operation in stallation repair and spare parts manual with each drying tumbler
Training tow engineers for 3 weeks in the factory
02-06-00254 | Flat work ironed machine |  |  |  |  | 500
electrically heated press roller to 1.5 m length automatic lifting and lowering of cylinder heat control finges - protection feeding and receving tables
connection to 380v 50hz 3ph
spare part list for 3 years
operation in stallation repair and spare parts manual with each drying tumbler
Training tow engineers for 3 weeks in the factory
02-06-00255 | Washing machine |  |  |  |  | 500
Capacity up to 50 kg/load (dry weight)
heating :steam (6-8 bar)
drumins stainless steel 18/8
operated by programme card and push botton for manual reverse drum action
safty look on door unbalance switch
G- factory :500 g
fitting and flexiable pipes 1.5 m in cluded
connection to 380 v 50 hz 3 ph
demostic water pressure supplied 0.5 bar
spare parts list for 3 years operation installation repair and spare parts manual with each washer
Training tow engineers for 3 weeks in the factory
02-06-00256 | Washing machine |  |  |  |  | 600
Capacity 20 kg/load (dry weight)
heating :electric element
drum stainless steel 18/8
operation by push botton for manual control reverse drum action
safty look on door
fitting and flexiable pipes 1.5 m in cluded
connection to 380 v 50 hz 3 ph
demostic water pressure supplied 0.5 bar
itemized and speratly priced spare parts list for 3 years operation installation repair and spare parts manual with each washer
Training tow engineers for 3 weeks in the factory
02-06-00257 | Washing machine |  |  |  |  | 600
Capacity 30 kg/load (dry weight)
heating :electric element
drum stainless steel 18/8
operation by programme card and push botton for manual reverse drum action
safty look on door
fitting and flexiable pipes 1.5 m in cluded
connection to 380 v 50 hz 3 ph
demostic water pressure supplied 0.5 bar
spare parts list for 3 years operation installation repair and spare parts manual with each washer
Training tow engineers for 3 weeks in the factory
02-06-00258 | Press |  |  |  |  | 400
Capacity 50 kg
02-06-00259 | hydro extractor |  |  |  |  | 600
Capacity 20 kg/load (dry weight)
G- factory :600-750 g
inner drum of stainless steel 18/8
timer operated reverse phase brake system
drive motor with thermal cut -out
vibration controlled inner drum
connection to 380 v 50 hz 3 ph
spare parts list for 3 years operation installation repair and spare parts manual with each washer
Training tow engineers for 3 weeks in the factory
02-06-00260 | Cornice flexiflame 70 |  |  |  |  | 400
02-06-00261 | Drying to LBG gas dryer |  |  |  |  | 100
02-06-00262 | Hot water boiler |  |  |  |  | 100
Capacity 2000 KG/hr
Working presser 10 bar
Automatic control for safe, starting and operation, automatic blow down valve, safety valve .
Burner : dual fuel L.P.G gas or light gas oil
Automatic operation isolated skid mounted ready for connection and operation
Softener : suitable duplex automatic operation softener suitable for boiler
Spear parts recommended for 5 years
Technical document / insulation / operation / martinets and repair
Training 3 engineers for one month in the factory
02-06-00263 | Calling system and equipment for calling system |  |  |  |  | 300
Complete paging system with its control station and 5 watt transmitter and 100 radio receives .
The system either independent or interfacing with telephone exchange
supply complete maintenance and operating installation catalog and spare pat catalog
02-06-00264 | Compressor |  |  |  |  | 50000
Specification of compressor 1/6 hp
Mod. FII 5IF IOG or FII 5IQ IOG
1/6 HP low back pressure static cooled R 12 compressor having following specification :
electrical characteristics
nominal voltage 220 V 50 HZ
voltage rang 170 - 240 V
power factor .95 ( shunt capacitor is to be used)
the compressor are to be supplied complot with starting device ( relay or ptc)
over load protector electrical connection board capacitor and the necessary wiring for electrical connection
dimensional data :
discharge tube 6.35 mm ID
suction tube 6.35 mm ID
process tube 6.35 mm ID
all tubing shall be made of high quality refrigerating copper tubes
Packing shall be made in strong wooden boxes or metallic cases suitable for shipment in containers and forklift handling.
02-06-00265 | Telephone exchange system
| 4X64 |  |  |  |  | 250
| 8 X 120 |  |  |  |  | 200
| 20 X 320 |  |  |  |  | 300
| 30X500 |  |  |  |  | 250
| 50 X 1000 |  |  |  |  | 100
| 10x250 |  |  |  |  | 100
| 10 x 75 |  |  |  |  | 100
| 150X2000 |  |  |  |  | 100
| 10X1000 |  |  |  |  | 100
each above internal extensions should be 80% analogue, and 20% digital
Auto communication switch system can use both type of telephone rotary dialing type and electronic push –bottom type programming of system facilities and read out should be accessible via data terminal
Facilities : consultation call with split call transfer three way conference executive station direct attendant call signaling camp on and over ride paging speed dialing restricted access for trunks call parking auto call back call forwarding manager secretary call interception busy over ride security group hunting UNA ANA
Tones : the system should be working on different tones such as internal ringing tone external ringing tone dial tone busy tone over ride tone hold or service tone confirmation tone call waiting tone order tone
Operator console : electronic push – bottom operator console can be connected at least 20 meters from the exchange required as communication link for incoming calls and external calls having more facilities than ordinary extenuation such as processing bottoms for arrival and departure callous call indication stand by and release automatic routine of calls serielcall over ride – camp on and hold external line reservation alarm display paging split and conference day timetransfer call tracking and toll display selftesting
Power supply : smooth and stabilized 48 V DC at 60 A max provided by main power parlor with 200 AH capacity battery accumulator which can deliver the power to the system for 5 hours in care of main failure
In case of 48 VPC failure to the system suitable battery back up supply electricity to 1000 hrs to different kind of memories to save stored elate.
Others :
1- Installation the system on sites and tow year maintenance
2- Spare parts for 5 years
3- Comet set of manuals installation maintenance programming and read out testing and trouble shouting.
4- Training on factory 5 engineers and 6 weeks
Equipment :pumps
model : as below
company / manufacturer : worthington
or equavalnt worthington
simpsonltd
low field works
p.o.box 17 newark , nottingh - amshire
NG243EN
ENGLAND
tel = newark 705151
tlx = 37451
quantity : 80
site : saddam medical city
| MOdEL | KW | HEAD (M) | FLOW (L/S) | RPM
02-06-00266 | 12LN21 | 340 | 36 | 650 | 1440 | 50
02-06-00267 | 12LN17 | 265 | 52.5 | 335 | 1440 | 50
02-06-00268 | 12LN17 | 224 | 36 | 372 | 1440 | 50
02-06-00269 | ERP80-400 | 150 | 140 | 30 | 2880 | 50
02-06-00270 | 12LA2 | 150 | 25.5 | 415 | 1440 | 50
02-06-00271 | 12LA2 | 90 | 30 | 300 | 1440 | 50
02-06-00272 | 10LA3 | 90 | 30 | 170 | 1440 | 50
02-06-00273 | 10LA3 | 90 | 43.3 | 142.3 | 1440 | 50
02-06-00274 | 65WP 315 | 75 | 132.5 | 22.5 | 2880 | 50
02-06-00275 | 6L3 | 55 | 32 | 101.29 | 1440 | 50
02-06-00276 | 6L3 | 55 | 52.5 | 52.24 | 1440 | 50
02-06-00277 | 65WP 315 | 55 | 103 | 22.5 | 2880 | 50
02-06-00278 | ERP60-200 | 45 | 190 | 7.57 | 2880 | 50
02-06-00279 | 50wp315 | 37 | 103 | 10 | 2880 | 50
02-06-00280 | 65WP 250 | 37 | 68.6 | 22.5 | 2880 | 50
02-06-00281 | 6L3 | 37 | 34 | 55.5 | 1440 | 50
02-06-00282 | 6L3 | 30 | 27 | 98.5 | 1440 | 50
02-06-00283 | 100WP200 | 30 | 37 | 43.1 | 2880 | 50
02-06-00284 | 80WP 160 | 15 | 24 | 30 | 2880 | 50
02-06-00285 | 1 ½ TM2 | 15 | 132.5 | 2.5 | 2880 | 50
02-06-00286 | 40WP 200 | 11 | 45 | 7.57 | 2880 | 50
02-06-00287 | 40WP 200 | 11 | 55 | 4.36 | 2880 | 50
02-06-00288 | 1 ¼ TM43 | 7.5 | 68.6 | 2.25 | 2880 | 50
02-06-00289 | 4L1 | 5.5 | 9 | 30.61 | 1440 | 50
02-06-00290 | 100WP200 | 4 | 11 | 17.42 | 1440 | 50
02-06-00291 | 1 ¼ TM22 | 4 | 83.3 | 1 | 2880 | 50
02-06-00292 | 3L1 | 3 | 8 | 15.86 | 1440 | 50
02-06-00293 | 3dv2 | 3 | - | - | 2880 | 50
02-06-00294 | 32wp160 | 1.5 | 14.6 | 2.25 | 2880 | 50
02-06-00295 | ELECTRICAL FORK LIFT (2 TON) |  |  |  |  | 400
1.MAXIM HEIGHT 7 TO 7.5 METER
2.FORK LENGTH 750 TO 1600MM
3. FORK CARRIAGE WIDTH 865
4.FORK WIDTH X THICKNESS 120X50
5.FORK SPREAD MAX 815
6. FORK SPREAD MINIMUM 455
7.OVER ALL WIDTH (AXLE BRACKET) 1450 OR 1500
8.LOAD WHEEL TRUCK 1310 OR 1370
9.REACH TRAVEL (MAX) 1220 TO 1625
10.LOAD WHEEL /LOAD CENTER 865 TO 1075
11.SWEEP RADIUS 815 TO 965
12.BOOM LENGTH TO PIVOT CENTER 865 OR 1015
13.LENGTH OF REACH FRAME 1320 TO 1725
14.FACE OF FORK TO PIVOT CENTER 455 TO 660
15.THROAT 965 TO 1805
16.BOOM / REACH FRAME HEIGHT 355
17.MECHANISM WIDTH 205
18.LOAD WIDTH 800 TO 1320
19.LOAD LENGTH 760 TO 1525
20.AISLE WIDTH 1525 TO 1930
21.ELECTRIC MOTORS-REACH 0, 4 KW
22.ROTATE 0, 4KW
23.FONK WIDTH MAXIM 1600 MM
02-06-00296 | ELECTRICAL FORK LIFT (1 TON) |  |  |  |  | 400
1.MAXIM HEIGHT 7 TO 7.5 METER
2.FORK LENGTH 750 TO 1600MM
3. FORK CARRIAGE WIDTH 865
4.FORK WIDTH X THICKNESS 120X50
5.FORK SPREAD MAX 815
6. FORK SPREAD MINIMUM 455
7.OVER ALL WIDTH (AXLE BRACKET) 1450 OR 1500
8.LOAD WHEEL TRUCK 1310 OR 1370
9.REACH TRAVEL (MAX) 1220 TO 1625
10.LOAD WHEEL /LOAD CENTER 865 TO 1075
11.SWEEP RADIUS 815 TO 965
12.BOOM LENGTH TO PIVOT CENTER 865 OR 1015
13.LENGTH OF REACH FRAME 1320 TO 1725
14.FACE OF FORK TO PIVOT CENTER 455 TO 660
15.THROAT 965 TO 1805
16.BOOM / REACH FRAME HEIGHT 355
17.MECHANISM WIDTH 205
18.LOAD WIDTH 800 TO 1320
19.LOAD LENGTH 760 TO 1525
20.AISLE WIDTH 1525 TO 1930
21.ELECTRIC MOTORS- REACH 0, 4 KW
22.ROTATE 0, 4KW
23.FONK WIDTH MAXIM 1600 MM
02-06-00297 | FORK LIFT (3 TON) |  |  |  |  | 150
1. DIESEL ENGINE 4 CYLINDER WATER COOLED
2. BATTERY 12V
3. NORMAL HYDRAULIC GEAR
4. MAX HEIGHT 3.5M
02-06-00298 | FORK LIFT (1 TON) |  |  |  |  | 150
1. DIESEL ENGINE 4 CYLINDER WATER COOLED
2. BATTERY 12V
3. NORMAL HYDRAULIC GEAR
4. MAX HEIGHT 3.5M
02-06-00299 | MEDICINES CARRYING TRUCKS: |  |  |  |  | 700
A- BASIC VEHICLE:
1. ENGINE: DIESEL ENGINE WATER COOLED
2. TRANSMISSION: MANUAL FLOOR SHIFT
3. CLUTCH: HYDRAULIC CONTROL SINGLE DRY PLATE WITH AIR PRESSURE ASSISTANCE
4. SUSPENSIONS: FRONT: LAMINATED LEAF SPRINGS WITH SHOCK ABSORBERS: REAR: FRONT: LAMINATED LEAF SPRINGS WITH SHOCK ABSORBERS
5. SUFFICIENT TO CONTROL THE VEHICLES IN THE PARKING SUPPLIED WITH AIR OVER HYDRAULIC WITH DUAL CIRCUIT
6. ELECTRICAL SYSTEM: 24V 120AMP
7. INSTRUMENT PANEL: ALL MEASUREMENTS AND GAUGES IN METRIC SYSTEM
8. FRAME: PARALLEL, TAPERED CHANNEL SECTION TYPE WITH CROSS MEMBERS AND REINFORCEMENTS
9. STEERING: LEFT HAND DRIVE, (BALL NUT TUBE, INTEGRAL TYPE) WITH HYDRAULIC POWER BOOSTER FLOOR SHIFT HANDLE
10.TIRES:HIGH QUALITY FRONT WHEELS: SINGLE IN EACH SIDE REAR WHEELS: DOUBLE IN EACH SIDE
11. DRIVERS CABIN: ONE AND HALF CABIN SUPPLIED WITH AIR-CONDITIONING SYSTEM (COOLING, HEATING AND VENTILATION)
12. EQUIPMENT’S: THE VEHICLES (TRUCKS) IT PROVIDES WITH ALL ACCESSORIES THAT ARE CONCERNING WITH WORK OF THE TRUCK
B- LOADING CAPACITY:
FIRST OPTION LOADING CAPACITY (2-4) TON QTY (25)
SECOND OPTION LOADING CAPACITY (5-7) TON QTY (250)
THIRD OPTION LOADING CAPACITY (8-10) TON QTY (25)
C-ACCESSORIES: EACH VEHICLE (TRUCK) SUPPLY WITH THE FOLLOWING:
FAST SPARE PART: AUTO JACK WITH HANDLE AND WHEEL WRENCH : HAZARD TRIANGLE: HYDRAULIC TAIL LEFT.
1. COOLING SYSTEM WORK BY ENGINE OR ELECTRIC POWER 380 VOLT 50 HZ 3 PHASE
2. DIAL THERMOMETER MUST BE PROVIDED
3. AUDIOVISUAL FOR HIGH TEMP. MUST BE FITTED
4. REFRIGERATION MUST SUITABLE TO MAINTAIN THE COOLING SPECIFICATION MENTION BELOW AND USES THE FOLLOWING GASES R12, R22, R502.
5. INTERNAL TEMP FROM + 10C TO-20C
6. AMBIENT TEMP.
SUMMER BDT 60C
WBT 25C
WINTER DBT 1C
WBT 3C
02-06-00300 | TRUCKS: |  |  |  |  | 700
C- BASIC VEHICLE:
1- ENGINE: DIESEL ENGINE WATER COOLED
2. TRANSMISSION: MANUAL FLOOR SHIFT
3. CLUTCH: HYDRAULIC CONTROL SINGLE DRY PLATE WITH AIR PRESSURE ASSISTANCE
4. SUSPENSIONS: FRONT: LAMINATED LEAF SPRINGS WITH SHOCK ABSORBERS: REAR: FRONT: LAMINATED LEAF SPRINGS WITH SHOCK ABSORBERS
5. SUFFICIENT TO CONTROL THE VEHICLES IN THE PARKING SUPPLIED WITH AIR OVER HYDRAULIC WITH DUAL CIRCUIT
C- ELECTRICAL SYSTEM: 24V 120AMP
7. INSTRUMENT PANEL: ALL MEASUREMENTS AND GAUGES IN METRIC SYSTEM
8. FRAME: PARALLEL, TAPERED CHANNEL SECTION TYPE WITH CROSS MEMBERS AND REINFORCEMENTS
9. STEERING: LEFT HAND DRIVE, (BALL NUT TUBE, INTEGRAL TYPE) WITH HYDRAULIC POWER BOOSTER FLOOR SHIFT HANDLE
10.TIRES:HIGH QUALITY FRONT WHEELS: SINGLE IN EACH SIDE REAR WHEELS: DOUBLE IN EACH SIDE
11.DRIVERS CABIN: ONE AND HALF CABIN SUPPLIED WITH AIR-CONDITIONING SYSTEM (COOLING, HEATING AND VENTILATION)
12.EQUIPMENT’S: THE VEHICLES (TRUCKS) IT PROVIDES WITH ALL ACCESSORIES THAT ARE CONCERNING WITH WORK OF THE TRUCK
B- LOADING CAPACITY:
FIRST OPTION LOADING CAPACITY (3-4) TON QTY (50)
SECOND OPTION LOADING CAPACITY (5-6) TON QTY (100)
THIRD OPTION LOADING CAPACITY (8-12) TON QTY (100)
C-ACCESSORIES: EACH VEHICLE (TRUCK) SUPPLY WITH THE FOLLOWING:
FAST SPARE PART: AUTO JACK WITH HANDLE AND WHEEL WRENCH HAZARD TRIANGLE
02-06-00301 | AMBULANCE |  |  |  |  | 400
PARTITION
BETWEEN DRIVER'S COMPARTMENT AND PATIENT’S COMPARTMENT FULL COVERAGE PANEL MADE OF STURDY MATERIAL (PRESS WOOD IS NOT TO BE USED) WITH SMOOTH SURFACE AT BOTH SIDE.
PARTITION WINDOW
LARGE, DOUBLE SLIDING SAFETY GLASS CENTRAL WINDOW
PATIENT'S COMPARTMENT
THE PATIENT'S COMPARTMENT IS TO BE FULLY INSULATED.
ROOF HEIGHT
INSIDE HEIGHT NOT LESS THAN 1500MM WITHOUT THE THICKNESS AND REINFORCEMENT.
FLOORING
HIGH QUALITY FLOORING MATERIAL CEMENTED TO A SUITABLE TYPE OF WOOD WITH ALUMINUM MOLDING.
MEDICINE CABINETS
THE LEFT WALL OF THE PATIENT’S COMPARTMENT IS TO BE PARTITIONED INTO ENCLOSED STORAGE CABINETRY. COMPARTMENT SPACE AND SHELF SPACE TO BE CONVENIENTLY LOCATED FOR MEDICAL SUPPLIES, DEVICES AND INSTALLED SYSTEM AD APPLICABLE FOR THE SERVICE INTENDED. CABINETS ARE TO BE EASILY OPENED WITH SHATTERED-PROOF TRANSPARENT SLIDING DOOR THE WALL IS TO BE NOT MORE THAN 30 INCHES HIGH. REMOVAL OF CABINET IS TO BE EASY TO FACILITATE BODY REPAIR IN CASE OF AN ACCIDENT.
TECHNICIAN SEAT - FRONT
PROVISION OF A TECHNICIAN SEAT AT THE FRONT OF THE PATIENT'S COMPARTMENT.
TECHNICIAN SEAT-REAR
PROVISION OF A TECHNICIAN SEAT AT THE FOOT OF THE PATIENT'S ON THE RIGHT END SIDE.
INSIDE LIGHTING SYSTEM
THE PATIENT'S COMPARTMENT ELECTRICAL SYSTEM IS TO BE SEPARATED FROM THE TRUCK.
IDENTIFICATION
THE AMBULANCE IS TO BE IDENTIFIED AS FOLLOWS:-
IT IS TO BE PAINTED CLEAR WHITE
- FOR DECALS FOR THE WORD "AMBULANCE", AND A RED CRESCENT IN ARABIC ONE ON EACH SIDE, ONE ON THE REAR, AND ONE ON THE FRONT
RESUSCITATION EQUIPMENT
- TWO OXYGEN BOTTLES, EACH OF 500 LITTER CAPACITY SECURED WITHIN THE LEFT WALL CABINETRY.
- TWO SPARE OXYGEN BOTTLES OF 500 LITTER CAPACITY IN STOWAGE CABIN.
- ONE SET OF ENGLISH BULL NOSE VALVE YOKE, PRESSURE REGULATOR WITH GAUGE FLOW METER AND HUMIDIFIER BOTTLE.
- THREE OXYGEN MASKS, ONE FOR EACH ADULT CHILD AND INFANT.
- THREE PLASTIC NASAL CANNULAS, TWO ADULT AND ONE CHILD.
- FOUR OXYGEN CATHETERS, TWO OF EACH NO.10F.
ONE MOUTH TO MOUTH VENTILATION MASK
| CYLINDER KEY |  |  |  |  | 1 FOR EACH
| OXYGEN FLOW METER /REGULATOR |  |  |  |  | 1 FOR EACH
| HUMIDIFIER |  |  |  |  | 1 FOR EACH
PORTABLE OXYGEN KIT
ONE PORTABLE OXYGEN KIT COMPETE WITH REGULATOR AND SUPPLIES.
| RESUSCITATOR COMPLETE WITH CYLINDER. |  |  |  |  | 1 FOR EACH
| RESTRAINING STRAP FOR RESUSCITATOR. |  |  |  |  | 1 FOR EACH
SUCTION SYSTEM
ONE VACUUM APPARATUS INCLUDING AN ELECTRIC DRIVEN PUMP with rechargable battery
FIRST AID EQUIPMENT
A BOX IS TO BE PROVIDED CONTAINING THE FOLLOWING:-
TWENTY PRE- LOCALIZED PADS
TWELVE COMPRESSIVE BANDAGES
- FOUR 10CM ELASTIC STRIPS.
- SIX GAUZE BANDEAUS, THREE OF 75MM AND THREE OF 150MM.
- TWENTY GAUZE PADS 10CM BY 10CM, INDIVIDUALLY WRAPPED.
- TWO 5CM ANTI-ALLERGIC ROLLS OF ADHESIVE TAPE.
FIFTEEN TONGUE DEPRESSORS INDIVIDUALLY WRAPPED.
- ONE 100 ML BOTTLE CONTAINING CHLOREXIDINE BASE DISINFECTANT.
AIR SPLINTS
ONE SET OF AIR SPLINT FOR EACH OF THE UPPER AND lower LIMBS.
STRETCHER
WHEEL STRETCHER WITH ADJUSTABLE BACK AND FOOT RESTS WITH SIDE HANDLES, COMPLETE WITH MATTRESS AND COVER.
SPARE STRETCHER
FOLDING COLLAPSIBLE STRETCHER WITH SUPPORTING SPREADER BARS AND VINYL COATED NYLON FABRIC.
REAR BUMPER STEP
A- REAR BUMPER STEP IS TO BE INSTALLED OVER THE REAR BUMPER.
BOTTLE HOOKS
BOTTLE HOOKS ARE TO BE INSTALLED ON THE ROOF TO HOLD FLUID AND BLOOD TRANSFUSION BOTTLES.
SPARE STRETCHER HOLDER
SPECIAL HOOKS ON WALL AND ROOF ARE TO BE PROVIDED TO HOLD SPARE STRETCHER WHEN REQUIRED.
EXHAUST-VENTILATOR FAN
ROOF MOUNTED DOUBLE ACTING EXH-VENT FAN IS TO BE INSTALLED.
REAR BUMPER STEP
A REAR BUMPER STEP IS TO BE INSTALLED OVER THE REAR BUMPER.
BOTTLE HOOKS
BOTTLE HOOKS ARE TO BE INSTALLED ON THE ROOF TO HOLD FLUID AND BLOOD TRANSFUSION BOTTLES .
ANTENNA
INSTALLATION OF RADIO ANTENNA IN EACH AMBULANCE AT THE ROOF.
WIRELESS EQUIPMENT: EACH AMBULANCE EQUIPPED WITH RADIO (WIRELESS COMMUNICATION DEVICE).
SPECIFICATIONS FOR AMBULANCES
BASIC VEHICLE
ENGINE: PETROL ENGINE WATER COOLED .
TRANSMISSION: MANUAL OR AUTOMATIC.
AXLE: SINGLE REAR OR FRONT WHEEL DRIVE.
STEERING :POWER STEERING LEFT HAND DRIVE.
SUSPENSION : HEAVY DUTY.
COOLING SYSTEM: HEAVY DUTY.
ELECTRICAL SYSTEM: 12 VOLTS WITH HEAVY DUTY ALTERNATOR AND BATTERY.
AIR CONDITIONING SYSTEM: AIR-CONDITIONER AND HEATER FOR BOTH DRIVER AND PATIENT COMPARTMENTS.
SIDE DOOR: SIDE DOOR AT THE RIGHT SIDE.
BACK DOORS: TWO PANEL DOORS OPENABLE TO THE SIDES.
INSTRUMENT PANEL: WITH METRIC GAUGES and ODOMETER.
MIRRORS: ONE INSIDE and TWO OUTSIDE REAR VIEW.
TIRES :HIGH QUALITY INCLUDING SPARE.
-WARNING EQUIPMENT: SIREN WITH SPEAKER AND BEACON OF THE FOLLOWING TYPES:
-ELECTRONIC SIREN WITH PUBLIC ADDRESS SYSTEM OF 100WATTS OUT-PUT POWER.
BEACON : TWO REVOLVING DOME TYPE BEACONS LONGITUDINAL A LONG THE WIDTH ON THE FRONT ROOF
-SPEAKER: 100 WATTS SPEAKER INSTALLED INSIDE ENGINE COMPARTMENT.
-ACCESSORIES:
AUTO JACK WITH HANDLE and WHEEL WRENCH.
TOOL KIT BAG.
HAZARD WARNING TRIANGLE
FIRE EXTINGUISHER.
-MISCELLANEOUS: THE FOLLOWING IS TO BE SUBMITTED TWO WEEKS AFTER ORDER CONFIGURATION:
-WORKSHOP MANUALS (2 COPIES IN ENGLISH).
-SPARE PARTS CATALOGUES (2 COPIES IN ENGLISH).
-RECOMMENDED SPARE PARTS LIST (DETAILS OF THE LIST ARE TO BE AGREED UPON).
FAST MOVING PARTS for EACH VEHICLE.
- TRAINING FOR 3 ENGINEERS.
optional rquipments schedule ambulance
| VACUUM MATTERS WITH CARRYING HANDLES. |  |  |  |  | 1 FOR EACH
| PUMP FOR VACUUM MATTRESS |  |  |  |  | 1 FOR EACH
| FOLDING STRETCHER |  |  |  |  | 1 FOR EACH
| INFLATABLE SPLINTS, SET OF 4 IN WALLET. |  |  |  |  | 1 FOR EACH
| ANALGESIC UNIT. |  |  |  |  | 1 FOR EACH
| NITRONOX CYLINDER (LIGHT WEIGHT) |  |  |  |  | 1 FOR EACH
| URINAL, MALE. |  |  |  |  | 1 FOR EACH
| URINAL, FEMALE. |  |  |  |  | 1 FOR EACH
| ORTHOPEDIC SCOOP STRETCHER |  |  |  |  | 1 FOR EACH
| BRACKETS FOR SCOOP STRETCHER. |  |  |  |  | 1 FOR EACH
| HEAPED AND HARDNESS SET FOR SCOOP STRETCHER. |  |  |  |  | 1 FOR EACH
| ASPIRATOR, MANUAL |  |  |  |  | 1 FOR EACH
| AMBULANCE CHAIR |  |  |  |  | 1 FOR EACH
| BRACKET FOR AMBULANCE CHAIR |  |  |  |  | 1 FOR EACH
| FIRST AID KIT COMPLETE WITH CASE. |  |  |  |  | 1 FOR EACH
| PENLIGHT |  |  |  |  | 1 FOR EACH
| BEDPAN |  |  |  |  | 1 FOR EACH
| ANEROID SPHYGMOMANOMETER |  |  |  |  | 2 FOR EACH
| STETHOSCOPE. |  |  |  |  | 2 FOR EACH
| OTOSCOPE. |  |  |  |  | 1 FOR EACH
| THOUGHT CUT SCISSORS. |  |  |  |  | 1 FOR EACH
| SEMI AUTOMATIC DEFIBRILLATOR /MONITOR |  |  |  |  | 1 FOR EACH
| SECURING DEVICE FOR DEFIBRILLATOR /MONITOR |  |  |  |  | 1 FOR EACH
| ARTERY FORCEPS (SPENCER WELLS) |  |  |  |  | 1 FOR EACH
| DISSECTING FORCEPS, PLAIN |  |  |  |  | 1 FOR EACH
| SCISSORS BANDAGE. |  |  |  |  | 1 FOR EACH
| THERMOMETER |  |  |  |  | 1 FOR EACH
| NON WOVEN ACRYLIC BLANKET 60"X80" APPROX. |  |  |  |  | 1 FOR EACH
| CELLAR BLANKET UNBLEACHED 60"X80" APPROX. |  |  |  |  | 2 FOR EACH
| FOAM PILLOW, PCV COVERED |  |  |  |  | 2 FOR EACH
| VACUUM FLASK STAINLESS STEEL 1 LITTER. |  |  |  |  | 2 FOR EACH
| RESTRAINING STRAP FOR VACUUM FLASKS |  |  |  |  | 1 FOR EACH
| OXYGEN CYLINDER, BULL NOSE (SIZE F) |  |  |  |  | 1 FOR EACH
| OXYGEN FACE MASK |  |  |  |  | 1 FOR EACH
| GREEN BUBBLE 30 FOOT ROLL |  |  |  |  | 2 FOR EACH
02-06-00302 | ACCIDENT EMERGENCY AMBULANCE |  |  |  |  | 200
PARTITION
BETWEEN DRIVER'S COMPARTMENT AND PATIENT’S COMPARTMENT FULL COVERAGE PANEL MADE OF STURDY MATERIAL (PRESS WOOD IS NOT TO BE USED) WITH SMOOTH SURFACE AT BOTH SIDE.
PARTITION WINDOW
LARGE, DOUBLE SLIDING SAFETY GLASS CENTRAL WINDOW
DOUBLE SLIDING SAFETY GLASS WINDOW BEHIND DRIVER CABINET ITS HEIGHT HALF INSIDE HEIGHT OF ROOF HEIGHT.
PATIENT'S COMPARTMENT
THE PATIENT'S COMPARTMENT IS TO BE FULLY INSULATED.
ROOF HEIGHT
INSIDE HEIGHT NOT LESS THAN 1900MM WITHOUT THE THICKNESS AND REINFORCEMENT.
FLOORING
HIGH QUALITY FLOORING MATERIAL CEMENTED TO A SUITABLE TYPE OF WOOD WITH ALUMINUM MOLDING.
MEDICINE CABINETS
THE LEFT WALL OF THE PATIENT’S COMPARTMENT IS TO BE PARTITIONED INTO ENCLOSED STORAGE CABINETRY. COMPARTMENT SPACE AND SHELF SPACE TO BE CONVENIENTLY LOCATED FOR MEDICAL SUPPLIES, DEVICES AND INSTALLED SYSTEM AD APPLICABLE FOR THE SERVICE INTENDED. CABINETS ARE TO BE EASILY OPENED WITH SHATTERED-PROOF TRANSPARENT SLIDING DOOR THE WALL IS TO BE NOT MORE THAN 30 INCHES HIGH. REMOVAL OF CABINET IS TO BE EASY TO FACILITATE BODY REPAIR IN CASE OF AN ACCIDENT.
TECHNICIAN SEAT - FRONT
| PROVISION OF A TECHNICIAN SEAT AT THE FRONT OF THE PATIENT'S COMPARTMENT. |  |  |  |  | 488
TECHNICIAN SEAT-REAR
PROVISION OF A TECHNICIAN SEAT AT THE FOOT OF THE PATIENT'S ON THE RIGHT END SIDE.
INSIDE LIGHTING SYSTEM
THE PATIENT'S COMPARTMENT ELECTRICAL SYSTEM IS TO BE SEPARATED FROM THE TRUCK.
IDENTIFICATION
THE AMBULANCE IS TO BE IDENTIFIED AS FOLLOWS:-
IT IS TO BE PAINTED CLEAR WHITE
- FOR DECALS FOR THE WORD "AMBULANCE", AND A RED CRESCENT IN ARABIC ONE ON EACH SIDE, ONE ON THE REAR, AND ONE ON THE FRONT
RESUSCITATION EQUIPMENT
- TWO OXYGEN BOTTLES, EACH OF 500 LITTER CAPACITY SECURED WITHIN THE LEFT WALL CABINETRY.
- TWO SPARE OXYGEN BOTTLES OF 500 LITTER CAPACITY IN STOWAGE CABIN.
- ONE SET OF ENGLISH BULL NOSE VALVE YOKE, PRESSURE REGULATOR WITH GAUGE FLOW METER AND HUMIDIFIER BOTTLE.
- THREE OXYGEN MASKS, ONE FOR EACH ADULT CHILD AND INFANT.
- THREE PLASTIC NASAL CANNULAS, TWO ADULT AND ONE CHILD.
- FOUR OXYGEN CATHETERS, TWO OF EACH NO.10F.
ONE MOUTH TO MOUTH VENTILATION MASK
PORTABLE OXYGEN KIT
ONE PORTABLE OXYGEN KIT COMPETE WITH REGULATOR AND SUPPLIES.
SUCTION SYSTEM
ONE VACUUM APPARATUS INCLUDING AN ELECTRIC DRIVEN PUMP.
FIRST AID EQUIPMENT
A BOX IS TO BE PROVIDED CONTAINING THE FOLLOWING:-
TWENTY PRE- LOCALIZED PADS
TWELVE COMPRESSIVE BANDAGES
- FOUR 10CM ELASTIC STRIPS.
- SIX GAUZE BANDEAUS, THREE OF 75MM AND THREE OF 150MM.
- TWENTY GAUZE PADS 10CM BY 10CM, INDIVIDUALLY WRAPPED.
- TWO 5CM ANTI-ALLERGIC ROLLS OF ADHESIVE TAPE.
FIFTEEN TONGUE DEPRESSORS INDIVIDUALLY WRAPPED.
- ONE 100 ML BOTTLE CONTAINING CHLOREXIDINE BASE DISINFECTANT.
AIR SPLINTS
ONE SET OF AIR SPLINT FOR EACH OF THE UPPER AND LIMBS.
STRETCHER
WHEEL STRETCHER WITH ADJUSTABLE BACK AND FOOT RESTS WITH SIDE HANDLES, COMPLETE WITH MATTRESS AND COVER.
SPARE STRETCHER
FOLDING COLLAPSIBLE STRETCHER WITH SUPPORTING SPREADER BARS AND VINYL COATED NYLON FABRIC.
REAR BUMPER STEP
A- REAR BUMPER STEP IS TO BE INSTALLED OVER THE REAR BUMPER.
BOTTLE HOOKS
BOTTLE HOOKS ARE TO BE INSTALLED ON THE ROOF TO HOLD FLUID AND BLOOD TRANSFUSION BOTTLES.
SPARE STRETCHER HOLDER
SPECIAL HOOKS ON WALL AND ROOF ARE TO BE PROVIDED TO HOLD SPARE STRETCHER WHEN REQUIRED.
EXHAUST-VENTILATOR FAN
ROOF MOUNTED DOUBLE ACTING EXH-VENT FAN IS TO BE INSTALLED.
REAR BUMPER STEP
A REAR BUMPER STEP IS TO BE INSTALLED OVER THE REAR BUMPER.
BOTTLE HOOKS
BOTTLE HOOKS ARE TO BE INSTALLED ON THE ROOF TO HOLD FLUID AND BLOOD TRANSFUSION BOTTLES .
ANTENNA
INSTALLATION OF RADIO ANTENNA IN EACH AMBULANCE AT THE ROOF.
WIRELESS EQUIPMENT: EACH AMBULANCE EQUIPPED WITH RADIO (WIRELESS COMMUNICATION DEVICE).
SPECIFICATIONS FOR AMBULANCES
BASIC VEHICLE
ENGINE: PETROL ENGINE WATER COOLED .
TRANSMISSION: MANUAL OR AUTOMATIC.
AXLE: SINGLE REAR OR FRONT WHEEL DRIVE.
STEERING :POWER STEERING LEFT HAND DRIVE.
SUSPENSION : HEAVY DUTY.
COOLING SYSTEM: HEAVY DUTY.
ELECTRICAL SYSTEM: 12 VOLTS WITH HEAVY DUTY ALTERNATOR AND BATTERY.
AIR CONDITIONING SYSTEM: AIR-CONDITIONER AND HEATER FOR BOTH DRIVER AND PATIENT COMPARTMENTS.
SIDE DOOR: SLIDING SIDE DOOR AT THE RIGHT SIDE.
BACK DOORS: TWO PANEL DOORS OPERABLE TO THE SIDES.
INSTRUMENT PANEL: WITH METRIC GAUGES and ODOMETER.
MIRRORS: ONE INSIDE and TWO OUTSIDE REAR VIEW.
-TIRES : 5 WITH TUBES, INCLUDING SPARE.
-WARNING EQUIPMENT: SIREN WITH SPEAKER AND BEACON OF THE FOLLOWING TYPES:
-ELECTRONIC SIREN WITH PUBLIC ADDRESS SYSTEM OF 100WATTS OUT-PUT POWER.
BEACON : TWO REVOLVING DOME TYPE BEACONS LONGITUDINAL A LONG THE WIDTH ON THE FRONT ROOF
-SPEAKER: 100 WATTS SPEAKER INSTALLED INSIDE ENGINE COMPARTMENT.
-ACCESSORIES:
AUTO JACK WITH HANDLE and WHEEL WRENCH.
TOOL KIT BAG.
HAZARD WARNING TRIANGLE
FIRE EXTINGUISHER.
-MISCELLANEOUS: THE FOLLOWING IS TO BE SUBMITTED TWO WEEKS AFTER ORDER CONFIGURATION:
-WORKSHOP MANUALS (2 COPIES IN ENGLISH).
-SPARE PARTS CATALOGUES (2 COPIES IN ENGLISH).
-RECOMMENDED SPARE PARTS LIST (DETAILS OF THE LIST ARE TO BE AGREED UPON).
FAST MOORING PARTS for EACH VEHICLE.
- ACCIDENT EMERGENCY TOOLS:
PREGNANCY
HOLDING CROWBAR
ELECTRICAL CUTTER
HYDRAULIC JACK WORK BY FOOT TO PULL MATERIAL PARTS.
AIR COMPRESSOR
HANDING CUTTER DIFFERENT SIZE
FIRE EXTINGUISHER (QTY 3)
TRANSMISSION TOOL (QTY 3)
- TRAINING FOR 3 ENGINEERS.
OPTIONAL EQUIPMENT’S SCHEDULE AMBULANCE
| VACUUM MATTERS WITH CARRYING HANDLES. |  |  |  |  | 1 FOR EACH
| PUMP FOR VACUUM MATTRESS |  |  |  |  | 1 FOR EACH
| FOLDING STRETCHER |  |  |  |  | 1 FOR EACH
| INFLATABLE SPLINTS, SET OF 4 IN WALLET. |  |  |  |  | 1 FOR EACH
| ANALGESIC UNIT. |  |  |  |  | 1 FOR EACH
| NITRONOX CYLINDER (LIGHT WEIGHT) |  |  |  |  | 1 FOR EACH
| URINAL, MALE. |  |  |  |  | 1 FOR EACH
| URINAL, FEMALE. |  |  |  |  | 1 FOR EACH
| ORTHOPEDIC SCOOP STRETCHER |  |  |  |  | 1 FOR EACH
| BRACKETS FOR SCOOP STRETCHER. |  |  |  |  | 1 FOR EACH
| HEAPED AND HARDNESS SET FOR SCOOP STRETCHER. |  |  |  |  | 1 FOR EACH
| RESUSCITATOR COMPLETE WITH CYLINDER. |  |  |  |  | 1 FOR EACH
| RESTRAINING STRAP FOR RESUSCITATOR. |  |  |  |  | 1 FOR EACH
| ASPIRATOR, MANUAL |  |  |  |  | 1 FOR EACH
| AMBULANCE CHAIR |  |  |  |  | 1 FOR EACH
| BRACKET FOR AMBULANCE CHAIR |  |  |  |  | 1 FOR EACH
| FIRST AID KIT COMPLETE WITH CASE. |  |  |  |  | 1 FOR EACH
| PENLIGHT |  |  |  |  | 1 FOR EACH
| BEDPAN |  |  |  |  | 1 FOR EACH
| ANEROID SPHYGMOMANOMETER |  |  |  |  | 2 FOR EACH
| STETHOSCOPE. |  |  |  |  | 2 FOR EACH
| OTOSCOPE. |  |  |  |  | 1 FOR EACH
| THOUGHT CUT SCISSORS. |  |  |  |  | 1 FOR EACH
| SEMI AUTOMATIC DEFIBRILLATOR /MONITOR |  |  |  |  | 1 FOR EACH
| SECURING DEVICE FOR DEFIBRILLATOR /MONITOR |  |  |  |  | 1 FOR EACH
| ARTERY FORCEPS (SPENCER WELLS) |  |  |  |  | 1 FOR EACH
| DISSECTING FORCEPS, PLAIN |  |  |  |  | 1 FOR EACH
| SCISSORS BANDAGE. |  |  |  |  | 1 FOR EACH
| THERMOMETER |  |  |  |  | 1 FOR EACH
| NON WOVEN ACRYLIC BLANKET 60"X80" APPROX. |  |  |  |  | 1 FOR EACH
| CELLAR BLANKET UNBLEACHED 60"X80" APPROX. |  |  |  |  | 2 FOR EACH
| FOAM PILLOW, PCV COVERED |  |  |  |  | 2 FOR EACH
| VACUUM FLASK STAINLESS STEEL 1 LITTER. |  |  |  |  | 2 FOR EACH
| RESTRAINING STRAP FOR VACUUM FLASKS |  |  |  |  | 1 FOR EACH
| OXYGEN CYLINDER, BULL NOSE (SIZE F) |  |  |  |  | 1 FOR EACH
| CYLINDER KEY |  |  |  |  | 1 FOR EACH
| OXYGEN FLOW METER /REGULATOR |  |  |  |  | 1 FOR EACH
| HUMIDIFIER |  |  |  |  | 1 FOR EACH
| OXYGEN FACE MASK |  |  |  |  | 1 FOR EACH
| GREEN BUBBLE 30 FOOT ROLL |  |  |  |  | 2 FOR EACH
02-06-00303 | CLINIC AMBULANCE |  |  |  |  | 70
(INTENSIVE CARE UNIT AND MOBILE THEATRE )
A- BASIC VEHICLE
1. ENGINE:- 4 or 6 or 8 clyinder
PETROL ENGINE
WATER COOLED
2. TRANSMISSION:- MANUAL GEAR BOX
FLOOR SHIFT
3. STEERING:- POWER STEERING
LEFT HAND DRIVE
4. ELECTRICAL EQUIPMENT’S:- 12- VOLT BATTERY
ANTENNA
INSTALLATION OF RADIO ANTENNA IN EACH AMBULANCE AT THE ROOF.
WIRELESS EQUIPMENT: EACH AMBULANCE EQUIPPED WITH RADIO (WIRELESS COMMUNICATION DEVICE).
5. SUSPENSION: HEAVY DUTY
6. TIRES:- HIGH QUALITY WITH TUBES
7. ACCESSORIES:-FIRE EXTINGUISHER
JACK
WHEEL WRENCH
TOOL KIT
FAST MOVING PARTS
B- PATIENT COMPARTMENT
1- RISE ROOF MORE THAN 1900MM INSIDE
2- HYDRAULIC STRETCHER (AS A TABLE OF THEATRE) MOVE FOR ALL THE DIRECTION. ( AND SHOCK ABSORBER )
3- ADDITIONAL BASE FOR HOLDING OF THE STRETCHER IN THE LEFT SIDE OF THE UNIT FIXED
4- ILLUMINATION: IN SIDE THE UNIT A FIXED SOURCES OF LIGHT USE FOR THE OPERATION IN THE UNIT SIDE MOVE FOR ALL DIRECTION AS NEED (LIKE OPERATIVE THEATRE)
5- EQUIPMENT FOR OXYGEN SUPPLY WITH SET FOR GIVING THE O2 COMPLETE (5 BOTTLE -2 BOTTLE 5000L +3 BOTTLE 500L)
6- ELECTRICAL SUCKER COMPLETE WITH ADDITIONAL PARTS PUT IN THE RIGHT SIDE OF THE UNIT (NEAR THE RIGHT HAND OF THE LIGHT)(portable with rechargable battery )
7- AIR CONDITIONING AND HEATING EMT
8- BOTTLE HOOKS 3 PARTS OF HOOKS IN THE ROOF FOR THE FLUID & BLOOD TRANSFUSION
9- STORE FOR THE MEDICAL DRUGS & INSTRUMENTS ALONG THE SPACE IN SIDE THE UNIT IN TWO SIDE RIGHT & LEFT WITH WASH BASIN IN THE LEFT CORNER OF THE UNIT
10- OXYGEN BOTTLE 5-7 500L & TWO MAIN SOURCES - BIG BOTTLE IN THE INSIDE UNIT (5000L) PUT IN DIFFERENT PRESS AS POSSIBLE
11- COMPLETE OXYGEN SET
12- ANAESTHETIC MACHINE COMPLETE holding
13-INTENSIVE CARE UNIT - MONITOR WITH DC. SHOCK (COMPLETE) + ECG+SPO2+NIBA+Paecmaker
14- ELECTRICAL SUCKER (COMPLETE) FIXED AT RIGHT HAND OF THE EMT(portable with UPS)
15- REFRIGERATOR FOR BLOOD STORAGE (MEDIUM SIZE )
16- SOURCE FOR OXYGEN READY FOR USE IN THE ROOF AT BOTH SIDES OF INSIDE THE UNIT
C- ADDITIONAL SUPPLIES:-
1- KIT - SET CONTAINING ALL INSTRUMENTS NEED FOR INTENSIVE CARE & ANAESTHETIC SUPPLIES & INSTRUMENTS SET WITH MASK OF 3 SIZE & ALL OTHER INSTRUMENT & SPHEGMAMONTER & STETHOSCOPE & OTHER SUPPLY COMPLETE
2- KIT FOR PORTABLE OXYGEN & COMPLETE ADDITIONAL PARTS FOR GIVING THE OXYGEN
3- SUCKER HAND & FOOT SUCKERS
4- AIR SPLINT FOR FRACTURES UPPER &LOWER LIMBS 2 SET FOR EACH
5- OXYGEN BOTTLE SPARE 5 BOTTLE 500 L
6- STRETCHER SPARE
1 RULING TYPES
1 FOLDING TYPES
1 PART SCOPE STRETCHER
1 AIR STRETCHER
7- KIT FOR FIRST AIDE CONTAINS COMPLETE INSTRUMENT FOR MINOR OPERATION & COMPLETE SET FOR BANDYING WITH SPHEGMONOMETER AND STETTUSCOPE
8- ULTRA VIOLET LIGHT INSTRUMENT FOR STERILIZATION UNIT & ANY OTHER THING FOR STERILIZATION SUITABLE IN THE UNIT
9- portable intensive care ventilator with UPS and patient cercuit
10- laryngeal mask (small ,medium, large)
11- 2 bottel for N2O with resulator and fitting to the anaesthetic machine
12- O2 regulator with fitting to the anaesthetic machine (qty 2)
13- O2 regulator with flow meter and humidifier for O2 mask therapy
02-06-00304 | EQUITMENT: RADIO (WIRELESS) COMMUNICATION NET WORK FOR EMERGENCY AMBULANCE CALLS. |  |  |  |  | 25 SYSTEM
CONSISTING OF THE FOLLOWING:-
- ALL NETWORK SYSTEM OPERATE IN FREQUENCY (420 MHZ-470MHZ)
NETWORK SYSTEM OPERATE WITH CODING - DECODING DEVICE
- ALL NECESSARY ANTENNA FOR THE FOLLOWING STATIONS WITH MAST (IF REQUIRED):
| CENTRAL STATION WITH DESK CONTROL AND UPS FOR 6 HOURS OPERATION: |  |  |  |  | 23
- TO OPERATE ALL CHANNELS FROM ANY DESK.
- DISPLAY FOR CODING AND DECODING SYSTEM
- DIGITAL CLOCK
- LAMPS FOR RECEIVING, TRANSMITTING AND STAND BY.
- SEMI-DUPLEX OPERATION (PUSH TO TRANSMIT)
- RF OUTPUT POWER SUFFICIENT TO COVER AN AREA 100 KM DIAMETER.
| FIXED STATION (8 CHANNELS): |  |  |  |  | 170
- TO COMMENCE WITH CENTRAL STATIONS AND OTHER FIXED STATIONS OR HANDY STATION.
- RF OUT PUT POWER NOT LESS THAN (10 RF WATTS)
- UPS FOR 6 HOURS OPERATION
- EXTRA LAUD SPEAKER.
| MOBILE STATIONS |  |  |  |  | 230
(AS FIXED STATION ABOVE) EXCEPT UPS
| HANDY STATION (WALK TALKY) |  |  |  |  | 70
TO COMMENCE WITH CENTRAL STATION and ALL OTHER STATIONS
| RECORDER SYSTEM |  |  |  |  | 25
- FOR RECORDING ALL MASSAGES DURING 24 HR.
- ALL OPTIONS FOR ABOVE ITEMS
- INSTALL ALL SYSTEM BY THE SUPPLIER
2 YEARS WARRANTY (SPARE + MEN POWER)
3 YEARS MAINTENANCE MEN POWER ONLY TRAINING FOR 4 FROM OUR TECHNICAL STAFF FOR 3 WEEKS FREE OF CHARGE.
* SPARE PARTS LIST WITH ITEM PRICE
* FULL CATALOGS (OPERATING AND MAINTENANCE WITH CIRCUIT DIAGRAM WITH EACH UNITS).
02-06-00305 | EQUIPMENT: |  |  |  |  | 400
WHEEL LOADER (1-2M3) BUCKET
DRIVER CABINS: FOLDING DOOR, THE LOCKING IS ASSURED ON AN OPEN POSITION. GLASS MADE OF SECURITY TYPE, THE SUSPENSION REDUCES SOUND VIBRATION. AIR-CONDITIONING DEVICE FOR DRIVER CABINS.
ENGINE: DIESEL ENGINE WATER-COOLED
GEAR BOX: INTEGRAL POWER SHIFT.
MOVING SPEEDS: SPEEDS IN KM/H
ELECTRIC EQUIPMENT: 24 VOLT 120 AMP
AXLES: FOUR WHEEL DRIVE: FRONT AXLE AND REVERSE AXLE
TIRES: HIGH QUALITY
BRAKES: HYDRAULIC SERVO BRAKES
PARKING BRAKES: DRUMS ON THE GEAR BOX.
STEERING: STEERING TOTALLY HYDRAULIC WITH CLOSED NEUTRAL POSITION.
HYDRAULICS: HYDRAULIC OPERATING WITH A DRIVE GEAR.
02-06-00306 | EQUIPMENT: |  |  |  |  | 40
ELEVATING WORK PLAT FORM ON TRUCK
BASIC VEHICLE:
1.ENGINE: DIESEL ENGINE WATER COOLED
2.TRANSMISSION: MANUAL FLOOR SHIFT
3.CLUTCH: HYDRAULIC CONTROL SINGLE DRY PLATE WITH AIR PRESSURE ASSISTANCE
4.SUSPENSIONS: FRONT: LAMINATED LEAF SPRINGS WITH SHOCK ABSORBERS: REAR: FRONT: LAMINATED LEAF SPRINGS WITH SHOCK ABSORBERS
5.SUFFICIENT TO CONTROL THE VEHICLES IN THE PARKING SUPPLIED WITH AIR OVER HYDRAULIC WITH DUAL CIRCUIT
6.ELECTRICAL SYSTEM: 24V 120AMP
7.INSTRUMENT PANEL: ALL MEASUREMENTS AND GAUGES IN METRIC SYSTEM
8.FRAME: PARALLEL, TAPERED CHANNEL SECTION TYPE WITH CROSS MEMBERS AND REINFORCEMENTS
9.STEERING: LEFT HAND DRIVE, (BALL NUT TUBE, INTEGRAL TYPE) WITH HYDRAULIC POWER BOOSTER FLOOR SHIFT HANDLE
10.TIRES:HIGH QUALITY FRONT WHEELS: SINGLE IN EACH SIDE REAR WHEELS: DOUBLE IN EACH SIDE
11. DRIVERS CABIN: ONE AND HALF CABIN SUPPLIED WITH AIR-CONDITIONING SYSTEM (COOLING, HEATING AND VENTILATION)
12. EQUIPMENT’S: THE VEHICLES (TRUCKS) IT PROVIDES WITH ALL ACCESSORIES THAT ARE CONCERNING WITH WORK OF THE TRUCK
13- EQUIPPED WITH FIBER GLASS CABINET, CAPACITY LOADING NOT LESS THAN 200 KG, HEIGHT NOT LESS THAN 10 METERS, HYDRAULIC CONTROL, SAFETY CONTROLS, SUITABLE TO REPAIR ELEVATED WINDOWS, EQUIPMENT AND LAMP POSTS … ETC.
02-06-00307 | TOWING TRUCK: |  |  |  |  | 200
SPECIFICATIONS FOR TOWING TRUCK:
A. BASIC VEHICLE:
1. ENGINE: PETROL ENGINE, WATER COOLED
2. TRANSMISSION: MANUAL FLOOR SHIFT AND ONE REAR SPEED.
3. DRIVE: 4 WHEEL DRIVE
4. STEERING: LEFT HAND DRIVE, (POWER STEERING).
5. SUSPENSION: HEAVY DUTY.
6. MIRRORS: ONE INSIDE AND TWO OUTSIDES SUITABLE FOR DRIVING THE VEHICLE.
7. BATTERY: (12 VOLT – 60 A.H) HEAVY DUTY.
8. TIRES: SEVEN TIRES WITH TUBES INCLUDING SPARE OF GOOD QUALITY.
9. CARBURETOR: SINGLE MANUAL CHOCK.
B. TOWING DEVICE:
1. BASIC RATING: 5 TONS
2. BOOM RATING:
FULLY RETRACTED (5 TONS)
FULLY EXTENDED.
3. WINCH RATING.
FIRST LAYER OF CABLE (5 TONS)
FOURTH LAYER OF CABLE (3 TONS)
4. LOAD CABLE:
TYPE 6 X 19 CLASS FIBER CORE IMPROVED PLOW STEEL.
DIAMETER AND STANDARD LENGTH (3/8 INCH X 10 FT),
WORKING LIMIT – SINGLE LINE (1 ½ TON) OR 3500 IBS).
NOTE –1- THE TOWING DEVICE SHOULD BE OPERATE BY BOTH MECHANICAL WAY DRIVEN BY THE GEAR BOX OF THE VEHICLE.
AND IN ANTHER WAY WE CAN USE IT BY ELECTRICAL WAY DRIVEN BY ELECTRICAL MOTOR DEPENDING ON THE ELECTRIC POWER OF THE VEHICLE.
NOTE-2- THE VEHICLE SHOULD BE SUPPLIED WITH ALL THE TOOLS NECESSARY FOR TOWING AND DRAWING AND LIFTING THE UNPREPARED CAR.
C. ACCESSORIES:
1. THE VEHICLE SHOULD PROVIDE WITH AUTO JACK AND FIRE EXTINGUISHER.
2. BOOKLET OF OWNER’S MANUAL (ENGLISH COPY).
02-06-00308 | EQUIPMENT: |  |  |  |  | 200
MOBILE CRANE
MOBILE CRANE, TELESCOPIC, FULLY HYDRAULIC, (20-30) TONS LOAD NOMINAL.
CARRIER PART:
ENGINE: DIESEL, WATER-COOLED, COMPLETE WITH ACCESSORIES, JACKS, EXTENSIONS, TOOLS.
TRANSMISSION: GEAR BOX, POWER SHIFT
TIERS: HIGH QUALITY
STEERING: HYDRAULIC SERVO- STEERING
BRAKES: SERVICE BRAKE: SERVO- BRAKE WITH COMPRESSED AIR ACTING ON ALL THE WHEELS.
DRIVER CABIN: MADE OF PLATE-STEEL RUBBER SUSPENSION, GLASS SECURITY WINDOWS, CONTROL INSTRUMENTS, ADDITIONAL SEAT FOR PASSENGER, AIR-CONDITIONING DEVICE.
ELECTRIC EQUIPMENT: 24 VOLTS, 120 AMP.
ROTATING PART:
ENGINE DIESEL WATER-COOLED.
CONTROLS BY HAND LEVERS AUTO-CENTERED DISTRIBUTORS.
CABIN: ALL STEEL. GLASS SECURITY WINDOWS, HEATING AND CONTROL INSTRUMENTS.
ELECTRIC EQUIPMENT: 24 VOLTS, 120 AMP.
02-06-00309 | EXCAVATOR, SMALL SIZE |  |  |  |  | 70
DRIVER CABINS: FOLDING DOOR, THE LOCKING IS ASSURED ON AN OPEN POSITION. GLASS MADE OF SECURITY TYPE, THE SUSPENSION REDUCES SOUND VIBRATION.
EARTH AND CONCERT DIGGING AND EXCAVATOR, SMALL MOBILE SIZE, DIESEL ENGINE, WATER-COOLED. FIELD TRUCK SUITABLE FOR DIGGING BURIED PIPES AND CABLES.
TIERS: HIGH QUALITY
ELECTRIC EQUIPMENT: 24 VOLTS, 120 AMP.
02-06-00310 | MOBILE DEAD BODY |  |  |  |  | 300
SPECIFICATION FOR MOBILE DEAD BODY CARRIER BASIC VEHICLES.
1- ENGINE: PETROL ENGINE
WATER COOLED
2- TRANSMISSION: MANUAL GEAR BOX – FLOOR SHIFT
4- BRAKE: DUAL- CIRCUIT HYDRAULIC BRAKE WITH VACUUM BOOSTER- SELF ADJUSTING MECHANICAL PARKING BRAKE
5- STEERING: POWER STEERING LEFT HAND DRIVE
6- FUEL TANK: 80 LITTER
7- BATTERY: 12 VOLT/ 75 AH
ALTERNATOR: 14V/90A
STATOR: 1.2KW
8- TIRES: HEAVY DUTY WITH TUBES
9- AIR CONDITION AND HEATING FOR DRIVER CABIN
10- ALL GANGES IN METRIC SYSTEM
11- PAINT: BLACK
12- ANTENNA
INSTALLATION OF RADIO ANTENNA IN EACH AMBULANCE AT THE ROOF.
WIRELESS EQUIPMENT: EACH AMBULANCE EQUIPPED WITH RADIO (WIRELESS COMMUNICATION DEVICE).
B- DEAD BODIES COMPARTMENTS TO BE COOLED BY A SUITABLE COOLING SYSTEM THAT MAINTAINED TEMPERATURE OF (10C) AT AN AMBIENT TEMPERATURE OF (55C) AND THE COOLING DEVICE IS SEPARATED FROM THE CAR ENGINE SHOULD BE FULLY ISOLATED FROM DRIVE CABINET FLOORING AND LINING OF SIDE WALL SHOULD BE OF CORROSION RESISTANT METAL OF SUITABLE THICKNESS JOINTS SHOULD BE WATER PROOF FOR CLEANING PURPOSES COMPARTMENT IS TO BE SUFFICIENTLY LIGHTED COMPARTMENT IS TO BE EQUIPPED WITH AN EXHAUST FAN.
LOADING DOOR: TWO REAR OPERABLE TO THE SIDE OR ONE RIG. FIXED STRETCHER TO BE FITTED IN A SUITABLE PLACE INSIDE THE VEHICLE WITH AN ADDITIONAL MOBILE STRETCHER.
C- ACCESSORIES: JACK WITH HANDLE AND WHEEL RANCH FIRE EXTINGUISHER REPAIR TOOL KIT OWNERS MANUAL (ENGLISH COPY)
02-06-00311 | VEHICLE PICK-UP SINGLE CABIN |  |  |  |  | 700
1. PETROL ENGINE WATER COOLED
2. MANUAL GEAR BOX, FLOOR SHIFT
3. STEERING POWER STEERING LEFT HAND DRIVE
4.ELECTRICAL EQUIPMENT’S: BATTERY 12V-60AMP HEAVY DUTY
5.AIR-CONDITIONING FOR DRIVER CABIN (HEATING AND COOLING)
6. SUSPENSION: HEAVY DUTY
7. TIRES WITH TUBES: SUITABLE FOR DIFFERENT ROADS (HIGH QUALITY)
8. CABIN: SINGLE CABIN WITH DOOR IN EACH SIDE.
9. MIRRORS: TO BE EQUIPPED WITH TWO SIDES MIRRORS AND ONE INSIDE
10.ACCESSARIES: TO BE EQUIPPED WITH JACK + WHEEL WRENCH + HAZARD TRIANGLE + TOOL KITS + FAST MOVING PARTS . WITH THE VEHICLE AND ANY EQUIPMENT’S CONCERNING THE JOB OF THIS CAR.
11.LOADING CAPACITY: FROM (1-2)TONS
12.ALL MATERIALS INSERTED IN THE CONSTRUCTION OF THIS CAR IT WILL BE OF HIGH QUALITY (ROOD, SHACKLE, GOODS COVER)
13.MAINTEMANCE FOR ALL VEHICLES FOR TWO YEARS ON ACCOUNT OF THE COMPANY WITH TRAINS FOR ENGINEERS AND TECHNICIANS (5PERISON) FOR ONE MONTH
02-06-00312 | LAND CRUISER 4 WHEEL DRIVER |  |  |  |  | 1250
1.PETROL ENGINE: ENGINE WATER COOLED
2.MANUAL GEAR BOX, FLOOR SHIFT
3.STEERING: POWER STEERING LEFT HAND DRIVE
4.ELECTRICAL EQUIPMENT’S: BATTERY 12V, 60AMP, HEAVY DUTY
5. AIR-CONDITIONING: TO BE EQUIPPED WITH EFFICIENT AIR-CONDITIONING SYSTEM FIT WITH OUR WEATHER (HEATING AND COOLING)
6.SUSPENTION: HEAVY DUTY
7.TIRES WITH TYPES SUITABLE FOR DIFFERENT ROADS (HIGH QUALITY)
8. DOORS: TWO DOORS IN EACH SIDE OF THE VEHICLE WITH REAR DOOR
9. MIRRORS: TO BE EQUIPPED WITH 2 SIDES MIRRORS AND ONE INSIDE
10. ACCESSORIES: TO BE EQUIPPED WITH JACK + WHEEL WRENCH AND HAZARD TRIANGLE AND ANY EQUIPMENT NECESSARY FOR JOB OF THIS VEHICLE
11. MAINTENANCE FOR ALL VEHICLES FOR 2 YEARS ON A COUNT OF THE COMPANY WITH TRAINS FOR ENGINEERS AND TECHNICIANS (5PERISON) FOR ONE MONTH
02-06-00313 | HANDLING TRUCKS |  |  |  |  | 500
FOR BOXES CASE (UP TO 300KG) WITH TOE EXTENDED (FOLD UP TOE) 2 WHEELS WITH RUBBER TIRES
02-06-00314 | LIGHT ALLOY TROLLEYS |  |  |  |  | 500
WITH ONE REMOVABLE ENDS. 350KG CAPACITY PLATE FORM OF ALUMINUM SLATS INSERTED IN A BOLTED, REIN FORCED FRAME AND CASTORS (2 FIXED AND 2 SWIVEL)
02-06-00315 | HAND PALLET TRUCKS |  |  |  |  | 500
CAPACITY UP TO 3000 KG
LIFTING: HYDRAULIC CONTROLLED BY HANDLE, RISE 120MM
CONTROL HANDLE: RETURNS AUTOMATICALLY TO UPRIGHT POSITION.
3 POSITION CONTROL HANDLE (RAISE, NEUTRAL, LOWER)
WHEELS 200MM STEERING WHEELS AND SIMPLE 85MM NYLON LOAD BEARING ROLLERS.
02-06-00316 | MOBILE LADDERS AND PLAT FORMS |  |  |  |  | 500
in ALUMINUM TREADS in NON SLIP STUDDED SURFACE
- PLATFORM IN ALUMINUM ALLOY, WITH NON SLIP STUDDED SURFACE. GUARD RAIL ON 3 SIDES, 1 SERVING AS TOOL RACK HEIGHT 1M.
- MAXIM PLAT FORM HEIGHT (3.5 METER)
- BASE FITTING FRONT 100MM Φ SWIVEL CASTORS WITHOUT BRAKE.
02-06-00317 | TELESCOPIC ELEVATING WORK PLATE FORMS |  |  |  |  | 100
- CAPACITY 360 KG FOLDED UP ALUMINUM ALLOY CONSTRUCTION MOUNTED ON 4 SWIVEL CASTORS (WITH EXTENDED LEGS)
- OPERATION: A HYDRAULIC SET INSTALLED AT THE BASE OF THE UNIT DRIVES 2 CYLINDERS (1 IN EACH MAST).
- POWER SUPPLY 220V AC AND 12V DC (OPTION)
- PLATE FORM DIMENSIONS 240 X 70 CM.
02-06-00318 | HIGH LIFT HAND PALLET TRUCKS 1000KG CAPACITY |  |  |  |  | 300
- FORK WIDTH 520 MM
MANUAL LIFT (HYDRAULIC)
- TO LIFT LOAD FROM 83 MM TO 830 MM (OR HIGHER)
LIFTING CONTROL: VIA PEDAL
LOWERING CONTROL: VIA HANDLE
02-06-00319 | NICKEL – CADMIUM ACCUMULATORS (BATTERIES) |  |  |  |  | 200
6 VOLT, 6 AH
02-06-00320 | EQUIPMENT: CLOCK
GROGY TIMING OLD MODEL GT1/60C1
| 1- CENTRAL CLOCK SYSTEM |  |  |  |  | 20
| 2- SINGLE FACE SLAVE CLOCK |  |  |  |  | 1200
| 3- DOUBLE FACE SLAVE CLOCK |  |  |  |  | 240
| 4- SPARE PART FOR 5-YEARS |  |  |  |  | 20 system
| 5- COMPLETE CATALOGUES SET |  |  |  |  | 24
6-installation of one system on site
7-guarrantee one year after installtion and operation
8-trining two-site egineer for two week at least on factory
02-06-00321 | SPECIFICATION OF AIRCONDITIONING |  |  |  |  | 250
WARE HOUSE (COLD STORE FOR DRUGS)
FIRST :
Supply and eraction (40) prefabricated air conditioning warehouse with the following specification
a- storing at temp 16-20 C
APPROXIMATE BUILDING DIMENTION:
100 m length
32 m width
8.3 m hight
| b- storing at temp 16-20 C |  |  |  |  | 10
APPROXIMATE BUILDING DIMENTION:
57 m length
20 m width
7 m hight
| c- storing at temp 15-20 C |  |  |  |  | 15
APPROXIMATE BUILDING DIMENTION:
25 m length
15 m width
5 m hight
3- frame work and roofing
a- main frames : the main frams will consist of hot rolled steel column , rafts without intermediate columns
b- purlins and side rails: purlins and side rails will be cold rolled pre galvanised material complete with all sleeves sagbars struts and bracings
c- ancillary steel work: the steel fram will be suppllied with all necessary gable steel work eavesties roof and vertical bracing door steel work and will be complete with foundation bolts and all eraction bolts
d-roofing:- single galvanised steel sheet 0.6 mm thick 45/250 profile poly esten coated with gutters 2mm thick golvanisid pressed steel down spout pipes high deusity pvc
e- servic preparation and treatment : all steel work will be sheet blasted during fabrication and primed with one coat height build zinc phosphate primer
4-CEILING AND SIDE WALL CLADDING:
a- insolated sandwich steel panel external and internal face 0.6 mm galvanised steel sheet ribbed with 4mm profile coated with 100 micron plastisol in standard color insulation 100 mm polyuerthene foam core density 40 kg/ m3 fixed with the maine fram
d- doors : each store has 4 no. ( 3500mm X 4500 mm) manually operated golvanised steel sheet slide doors both side with insulation 100mm polyurethene and curtain
e- an inter area 25X8 m in the front and back side of the store to keep the cold air provided with two doors (4000mmX4000mm) in each side and with curtain
f-an office 4000mmX4000mmX2800mm inside each store from sandwich panal provided with split unit for air condtioning 2 TR with PVC floor tiles
5- cold stor ( one pore each stor ) 200 m3 capacity prefabricated insulated panal 120mm polurethane density 40 kg/m3 . Tempreture range (0-4)C . Anbient temp 50C internal face 0.6 mm aluminum sheet external face 0.6mm galvanised steel sheet coated with plastisol 100 mm micron floor anti - slip aluminum ( jacker) tow cooling units
6-AIR CONDITIONING INSTALLATION :
SUPPLY AND INSTALLEDAIR COOLED PACKAGED WATER CHILLERS ONE STAND BY WITH CENTERFUGAL PUMPS AND AIR HANDLING UNITS AND CELLING FAN COIL . IN SIDE TEMP (16-20)C AMBIENT (EXTERNAL) TEMP 50C
7- electrical installation :
a- transformer with suitable capacity and all hight tension equipment and cabling
b- main switch boardse and distribution boards mounted out side the store
c- cabling / sub - circuits wiring
d- lighting : provided from floresent fitting (double flouresent ) 20 w/m2 with reflector (tld 36 w) for inside the store and hp sodium 250 w with fitting for outside
8-fire alarm system : acomplete fire alarm system comprising break glass points on fire exit doors and sirens to give audibility throughout the building and with sensors ( smoke , heat , radiation ) with wire and cable complete with all necessary fitting and terminations ( control boarde)
9-fire fitting system ( automatic sprinkler system) design manufacture deliver and installation of an automatic roof sprinklers system in each store including the following equipment per store and fire extignation
a- all pipe work fittings hangers and sprinklers heads
b- all necessary installation controlling valve
c-two automatic fire pumps ( one electrical and the others is diesl with all boards
d- water storage tank enough for one hour made from galvamised steel
e- joky pump
10- storage racking : storage racking type narrow aisel racking from galvanside steel hight 6100 mm ther pore allowing 6 pallet high stacking per bay the bay dimension is 2x1000 mm width x1200 mm deep the distance between racking (1700-1800)mm
11- frok lift truck:
a-two frok lift per stor.for the racking rider electric reach truck which operates in narrow gang ways.(side laoiking)
capicity 1350 KG lifting height 7000mm tyres.driver/steer-cushion rubber load/buthane/polyuretheue width. max. 1600mm battery 48V with charger them 8 hours 229/25V AC single phase 50HZ
b-two frok lift per stor / for loading and unloading from the truck capacity 1350KG liting hight 2500-3000mm with battery 24V
12-generator one generator for each stor 500KVA water cool,turdo charger,sound and whether proof container.
13-one electronic.digital (PABX),6 trunk,64 extension with all necessary equpment,UPS power suply MDF.and telephon set.
SECOND: general condition
1-the offer should include work shope drawing for foundation and mechanical ,electrical-fire fighting
2-one year waramty 1 spare parts and labour.
3-one year mainten ance labour only
4-foumdation will be don by the eliemnt according to your design and drawing
5-stor building to risut 140KM/Hr
6-supply quick moving spare part list enough for five yeas
7-the company shoulds submit training course for 6 technicians for three weeks and am invitation for 4 engineers for observation for two weeks
02-06-00322 | Telephone exchange system |  |  |  |  | 50
Capacity :1000 line
10% of lines for special
02-06-00323 | Packaged unit air-conditioning 12 ton for lift room |  |  |  |  | 70
02-06-00324 | Equipment: Multimedia projector |  |  |  |  | 200
minimum specification
- 650 ANSI Lumens
- SVGA (800X600) on – screen resolution
- Portable 8.2 Kg
- 4on- screen presentation tools
- full remote control with “ virtual mouse “
- screen image size (diagonal) : 53 CM to 762CM
- four in put channels for computer and video signals
- built-in speakers and audio in puts for external connection
02-06-00325 | Equipment : Scanner |  |  |  |  | 200
-push – button scanning
- full 36 – bit cooler depth ( in put and out put)
- solid steel chassis
- fast single – pass scanning
- quick easy – to – install enhanced parallel ( EPP) inter face ( no. SCSI card necessary )
- 600 X 1200 DPI optical resolution
- 9600X9600 DPI enhanced resolution
- Arabic and English OCR +caress Omni page softwares
02-06-00326 | Equipment : notebook |  |  |  |  | 200
- intel pentium II 300 MHZ with MMX TECHNOLOGY
- Intel mobil module (IMM) architecture
- 128 Mb EDO DRAM
- 512 KB secondary cache
- 9GB HDD
- 1.44 Mb modular floppy drive
- 24X CD- ROM ( optional DVD- ROM drive )
- 13.3” TFT screen / XGA screen
- integrated 16-bit stereo sound system
- NTSC/PAL TV out and s-video out
- S3 Virge MX/ 4Mb (videschip/RAM)
- PCMCIA 56K integrated fax modem
- 232-bit card, 1zoomed vides (PC card slot)
- (Battery/life) lithium ion/2.9 hours
- (Dimensions/ Travel weight) 2.1x12x9.5”/8.6 pounds
- USB and fast IR ports
- Integrated personal touch pad
- 2 extra Battery and charger for eash Unit
- VDC connecter
02-06-00327 | EQUIPMENT:ROOF |  |  |  |  | 100000M2
- U Value Kcal/m2 hc: 0.55-0.74
- Weight/Kg/m2: 12.51
- Length/m: 6-9
- External face 0.63mn galvanised steel sheet 0.45mm profile coated with 25 microns superacrulic in standard colour. Iinternal face 0.63mm thick galvanised steel sheet ribbed with 4mm profile coated with 25micron suberacrylic in standard colour Insulation 30mm polyurethene foam core density 40-50KG/m3
02-06-00328 | EQUIPMENT:WALLS |  |  |  |  | 30000 m2 with angle and Tee elements
- U Value Kcal/m2hc: 0.55-0.74
- Weight/Kg/m2: 12.51
- Length/m: 6-9
- External and Internal face 0.63mm galvanised steel sheet with 4mm profile coated with 25 micron superacrylic in standard colour. Insulation 30mm polurethene foam core. Density 40-45 Kg/m3
02-06-00329 | Offset machine four colors size 72x102cm |  |  |  |  | 50
02-06-00330 | Offset machine . four colors size 52x74cm with numbering system |  |  |  |  | 50
02-06-00331 | Offset machine size 36x52cm four colors with numbering system |  |  |  |  | 50
02-06-00332 | Camera photo for off set with drum scanning and all accesries |  |  |  |  | 50
02-06-00333 | Device Contact size :100 X 150 |  |  |  |  | 50
02-06-00334 | Stitching machine with four heads four size 20x25mm |  |  |  |  | 50
02-06-00335 | Machine of tying string |  |  |  |  | 50
02-06-00336 | Collection machine for all sizes |  |  |  |  | 50
02-06-00337 | High speed paper cutter (width 115cm) with ten knives as spare |  |  |  |  | 50
02-06-00338 | Inking operator for GTO machine size . 32 X 46 cm |  |  |  |  | 50
02-06-00339 | Inking operator for GTO machine size : 35 X 52 cm |  |  |  |  | 50
02-06-00340 | Numbering box letter press for 6 numbers back down |  |  |  |  | 3000
02-06-00341 | FILM ARTS GRAPHICS BLACK & WHITE
| Size : 50 X 60 cm |  |  |  |  | 3000
| 100X70 CM |  |  |  |  | 3000
| 40 X 60 cm |  |  |  |  | 3000
02-06-00342 | Set . of light notes to dark notes that |  |  |  |  | 20
Return to picture .
02-06-00343 | plate pressing size : 102X71 cm |  |  |  |  | 200 boxs each box 100 sheet
|  |  | 52X74 cm |  |  | 200 boxs each box 100 sheet
|  |  | 32X 46 cm |  |  | 200 boxs each box 100 sheet
02-06-00344 | Blanket size : 102X71 cm |  |  |  |  | 4000
|  | 50X74CM |  |  |  | 4000
|  | 32X52 cm |  |  |  | 4000
|  | 32X46 cm |  |  |  | 4000
02-06-00345 | Under blanket size: 102X71 cm |  |  |  |  | 4000
|  |  | 52X74CM |  |  | 4000
|  | 32X52 cm |  |  |  | 4000
|  | 32X46 cm |  |  |  | 4000
02-06-00346 | Developer plate A & B |  |  |  |  | 3000 for each
02-06-00347 | Correction |  |  |  |  | 200 bottle
02-06-00348 | Fixer |  |  |  |  | 200 bottle
02-06-00349 | Ster lon sheet 100X70 cm |  |  |  |  | 4000 sheet
02-06-00350 | Steel core for switching machine 22\19& 21\19 |  |  |  |  | 2000 turning
| copper core for switching machine 22\19& 21\19 |  |  |  |  | 2000 turning
02-06-00351 | Cart bort 100 X70 cm , 240 g\m |  |  |  |  | white coloer20000 band
| Cart bort 100 X70 cm , 240 g\m |  |  |  |  | green coloer 20000 band
| Cart bort 100 X70 cm , 240 g\m |  |  |  |  | blue cooler 20000 band
| Cart bort 100 X70 cm , 240 g\m |  |  |  |  | pink coole20000 band
02-06-00352 | Cart bort 100 X 70 cm ,200 g\m |  |  |  |  | white cooler 20000 band
| Cart bort 100 X 70 cm ,200 g\m |  |  |  |  | green coloer 20000 band |  | 77
| Cart bort 100 X 70 cm ,200 g\m |  |  |  |  | blue coloer 20000 band
| Cart bort 100 X 70 cm ,200 g\m |  |  |  |  | pink coloer20000 band
02-06-00353 | Cart bort 100 X70 cm ,180 g\m |  |  |  |  | white coloer 20000 band
| Cart bort 100 X70 cm ,180 g\m |  |  |  |  | green coloer 20000band
| Cart bort 100 X70 cm ,180 g\m |  |  |  |  | blue color 20000 band
| Cart bort 100 X70 cm ,180 g\m |  |  |  |  | pink coloer 20000 band
02-06-00354 | Paper 100 X 70 cm , 80 gm , |  |  |  |  | white coloer 20000 band
| Paper 100 X 70 cm , 70 gm , |  |  |  |  | white color 20000 band
| Paper 100 X 70 cm , 60 gm , |  |  |  |  | white coloer 20000 band
02-06-00355 | Inking off set |  |  |  |  | 2000sets & 6000 kg black
02-06-00356 | Inking letter |  |  |  |  | 1000 & 1000 kg black
02-06-00357 | Carbon papers 100X70 cm |  |  |  |  | white coloer 5000 band
| Carbon papers 100X70 cm |  |  |  |  | blue coloer 5000 band
| Carbon papers 100X70 cm |  |  |  |  | pink coloer 5000 band
| Carbon papers 100X70 cm |  |  |  |  | yellow coloer 5000 band
EQUIPMENT: SUB – STATION
SITE:SADDAM MEDICAL CITY
02-06-00358 | STEPDOWN TRANSFORMER DELTA/ STAR 11000/400VOLT, 3500KVA, 50HZ,DRY TYPE,TOTALLY ENCLOSED, INDOOR MOUNTED AND SHALL BE BUILT IN ACORDANCE WITH THE LATEST SPECIFICATION OF BS AND\OR IEC |  |  |  |  | 50
115 C RISE ABOVE 50 C AMBIANT , CAPABLE OF CARRYING 15% CONTINUOS OVERLOAD WITHOUT EXCEEDING A 150 C RISE
02-06-00359 | A COMPLETE HIGH VOLTAGE SUB-STATION CAPABLE OF FEEDING 3 TRANSFORMERS ; ONE SWITCHGEAR FOR EACH AND A MAIN INCOMMING FEEDER |  |  |  |  | 20
THE H.V SWITCHGEAR SHALL BE HORIZONTAL DRAW OUT C.B ,INDOOR CONSTRUCTION ,WEATHER PROOF , VOLTAGE RATTING 15 KV, SYSTEM VOLTAGE 11 KV, 3 PHASE, 3 WIRE, 50 Hz.
DESIGNED MANUFACTURED AND TESTED ACCORDING TO THE BS AND\OR IEC CODE ,WITH ALL PROTECTION AND METERING EQUIPMENTS , THE BREAKER SHAL BE OPERATED BY A MOTOR CHARGED SPRING THE STORED ENERGY MECHANISIM, 110 OR 24 VDC AND IN AN EMERGENCY BY A MANUAL HANDLE, THE SUB-STATION SHALL CONSISTS OF A DC CHARGER 110V OR 24V
02-06-00360 | MEDIUM VOLTAGE SWITCH BORD MAIN AND TIE CB, SHALL CONSIST OF 3-MAIN INCOMMING FEEDERS FROM THE TRANSFORMERS AND 9-OUTGOING FEEDERS TO FEED 9-CHILLERS OF 1508 AMP EACH, AND 2 TIE BREAKER AND SHALL BE INTERLOCKED WITH THE MAIN BREAKERS SO BOTH BREAKERS CAN NOT BE CLOSED SIMULTENEOUSLY. |  |  |  |  | 10
THE MAIN AND TIE CB’S SHALL BE THE FUSED DRAWOUT TYPE, MECHANICALY AND ELECTRICALY OPERATED AIR CB’S , WITH ALL PROTECTION AND METERING EQUIPMENTS , CALIBRATIONS AND ADJUSTMENTS SHALL BE IN ACCORDANCE WITH I.E.C STANDERDS
02-06-00361 | BUSWAYS 5000 AMP. RATING |  |  |  |  | 200
| PROVIDE TOTALLY INCLOSED WEATHER PROOF LOW IMPEDANCE BUS WAYS BETWEEN TRANSFORMERS SECONDARIES AND M.V MAINSWITCH BORDS , COMPLETE WITH INCLOSURE , ELBOWS , FITTINGS SUPPORTS , HANGING DEVICES ,ACCESSORIES, CABLE TAP BOXES. |  |  |  |  | METERS
BUSWAY SHALL BE 220/380 V , 3 PHASE ,4 WIRE , 50 Hz .
BUSBARS SHALL BE COPPER FABRICATED FROM 98% CONDUCTIVITY COPPER ,SILVER PLATED OVER THE INTIRE LENGTH
02-06-00362 | Field car ( 4WD a/c model 99 ) |  |  |  |  | 200
LAND CRUISER 4 WHEEL DRIVER
1.PETROL ENGINE: ENGINE WATER COOLED
2.MANUAL GEAR BOX, FLOOR SHIFT
3.STEERING: POWER STEERING LEFT HAND DRIVE
4.ELECTRICAL EQUIPMENT’S: BATTERY 12V, 60AMP, HEAVY DUTY
5. AIR-CONDITIONING: TO BE EQUIPPED WITH EFFICIENT AIR-CONDITIONING SYSTEM FIT WITH OUR WEATHER (HEATING AND COOLING)
6.SUSPENTION: HEAVY DUTY
7.TIRES WITH TYPES SUITABLE FOR DIFFERENT ROADS (HIGH QUALITY)
8. DOORS: TWO DOORS IN EACH SIDE OF THE VEHICLE WITH REAR DOOR
9. MIRRORS: TO BE EQUIPPED WITH 2 SIDES MIRRORS AND ONE INSIDE
10. ACCESSORIES: TO BE EQUIPPED WITH JACK + WHEEL WRENCH AND HAZARD TRIANGLE AND ANY EQUIPMENT NECESSARY FOR JOB OF THIS VEHICLE
11. MAINTENANCE FOR ALL VEHICLES FOR 2 YEARS ON A COUNT OF THE COMPANY WITH TRAINS FOR ENGINEERS AND TECHNICIANS (5PERISON) FOR ONE MONTH
02-06-00363 | Photo copy machine |  |  |  |  | 100
02-06-00364 | Overhead projector , LAMP 650 W , 25  25 cm |  |  |  |  | 100
02-06-00365 | Television ( 39 inch ) |  |  |  |  | 100
02-06-00366 | Video camera ( VHS ) with accessories |  |  |  |  | 100
02-06-00367 | Double- cassette recorder with amplifier |  |  |  |  | 100
02-06-00368 | Video ( VHS ) with accessories |  |  |  |  | 100
02-06-00369 | Photo Camera |  |  |  |  | 100
02-06-00370 | Slide projector with all accessories |  |  |  |  | 100
02-06-00371 | Assembly of video – tape equipment ( for recording , play – back & editing ) (VHS system) |  |  |  |  | 100
02-06-00372 | Pentium I I -450 MH3w/cache |  |  |  |  | 200
128-MB RAM
6-MB HDD
1.44-MB FDD
40-X CD Drive
Multimedia KIT
-8 MB VRAM
-A/E 104 Keys Keyboard
MS mouse + Pad
-Power Supply + Case+
Dust Covers
-15n Monitor SVGA
*HP Laser jet 1100
Printer
Extra Tones 10 foe each
Printer
HP 6P Laserjet printer( 2 only )
02-06-00373 | passenger bus for transportation of wheel chair patient
| capasity :- 6-10wheel chair aoutomatie door with hydrolic lifter for wheel chair diesel engine ,air condition ,tow ordinary seats and flat floor |  |  |  |  | 50 Buses
02-06-00374 | VACUM AIR |  |  |  |  | 20
02-06-00375 | Telephone exchange system |  |  |  |  | 20
2 out line x 20 in line
02-06-00376 | EQUIPMENT: Generator (1000KVA ) |  |  |  |  | 600
| Generator (250KVA) |  |  |  |  | 600
| 1500 KVA |  |  |  |  | 50
| 750 KVA |  |  |  |  | 75
| 550 KVA |  |  |  |  | 270
|  |  |  | 150KVA |  | 90
|  |  |  | 55 KVA |  | 1000
Fully automatic mains failure diesel generator sets suitable for operation in tropical dusty atmosphere at ambient temp. Ranging from 0C-60 C and humidity 95% on weather sound proof container for (1500 ,750 , 550)KVA and weather proof canopy with sufficient place for maintenance and repairing.
Prime power : (1500,750,550,55) KVA
Nominal voltage : 400V
Nominal frequency : 50 HZ
Speed : 1500 rpm
Power factor : 0.8
Voltage variation : static + _ 1-1.5 %
Alternator connection star with neutral
Insulation class F rotor and stator
temperature rise class F rotor and stator
- harmonic distortion factor < 3.5 %
- construction B3/B5
- radio interference class N
- tropical insulation
-long life bearings
Damper winding for parlor operation 100% unbalanced
Load
Ambient temp. 0-60 C , humidity 95%
Fuel tank 10 hours at full load operation Starting battery capacity 240 AH ,voltage 24 V for
(1500,750,550)KVA, 12V 120 AH for
55KVA
Time delay on starting 0-60 second
On release 0-15 minutes
Over load operation 10% for one hour
The diesel engine, (know manufacturing origin ,first oil filling , water cooled with turbocharger intercooler for 500 KVA and above electronic speed governer )1s rigidly coupled with synchronous alternator (know manufacturing origin ,self exiting self regulating revolving field Brushles automatic voltage regulation) and mounted on a common base frame and probably connected electrically and mechanically to control panel which is designed for full automatic operation with status indication.
The set engine and alternator and control panel is equipped with all accessories needed for sensing indicating warning metering protecting and supervision the flowing:
1- starting failure
2- over and under voltage
3- over and under speed
4- Oilpressure and temp.
5- low fuel level
6- Water pressure and temp.
7- phase failure and sequence
8- Over load and short circuit.
9- battery failure
10- lubrication system failure
11- cooling and pre-heating system failure
12- fuel injection system failure
13- Alternator winding and bearing temp.
14- alternator over current
And also the control panel should contain the followings :
1- pair of change over contractors mechanically & electrically interlocked
2- circuit breaker fitted with thermal overload trips & magnetic short circuit release , the generator .
3- automatic battery charger device 220/24 volt with voltmeter & ampere meter for starter battery voltage & current , MCB for charging device , switch on/off for battery voltmeter , indication of failure in battery system
4- manually operated change - over switch to connect load directly to network to facilitate isolation & maintenance of control panel
5- time delay to isolate load from generator & connecting it to the main power setting one minute
And also ) Electric lighting must be sufficient inside the container at least 6 florescence (40 watt ,220 volt for each fluorescence) and 20 watt , 220V for the outside control panel
The offer including :
1-.installation the gensets on sites
2- spare part for 5-years
3-warranty period of tow years after operation at site
4-three years maintenance after period of warranty
5-training course on factory
6-complete standard set of tools and measuring equipment for each set
7-complete set of mantas and diagram for each set
02-06-00377 | Electric drill |  |  |  |  | 50
02-06-00378 | Dishes washing machine |  |  |  |  | 50
02-06-00379 | Ampoule sealing machine with accessories |  |  |  |  | 50
02-06-00380 | Cold room |  |  |  |  | 100
35C 9.5M3
02-06-00381 | Cold room |  |  |  |  | 100
+2/+6 C 7.2M3
02-06-00382 | Security system |  |  |  |  | 50
02-06-00383 | Specific printer for bar |  |  |  |  | 300
02-06-00384 | Lab refrigerators |  |  |  |  | 50
02-06-00385 | Vacuum |  |  |  |  | 20
02-06-00386 | VEHICLE |  |  |  |  | 150
Mechanical Specification Fire Fighting ( Water + Foam Vehicle )
1. The Cabin :
A: Left hand drive with power steering
B: Six seat including the driver ( double cabin ) .
C: Anti corrosion made cabin .
D: Provided with unbreakable glass.
E: The Cabin provided with hydraulic & manual system for rising
F: red paint .
2. The Engine :
A: Working by fuel ( Diesel ) in line .
B: Provided with prefect water cooling system for the engine of the vehical
C: The horse power not less than ( 300 ) with one axle .
3. The pump unit :
A: Type – centrifugal combined for normal & high pressure with four stages .
B: Material – anti corrosion –impellers , suction inlet , discharge outlet , pump shaft made of stainless steel .
C: Power take off : with gear , oiling system , mechanical pneeumatic engagement , disengaement , control located cabin .
D: Pump outlet not less than 3000 liter / min at (8-10) bar .
E: Provided with automatic outlet air system .
F: Provided with one suction system in each side within (4) inch diameter ( English teech ) with cover strainer .
G: Provided with four outlet 2,5 inch ( Tow in each side or in the rare ) instantaneous coupling .
H: Proviede with all gauge for pressure & speed pump .
4. Water Foam Tank :
A: 7000-7500 liter water + at least ( 500 – 1000 ) liter foam .
B: Water & Foam tank made from suitable material unit corrosion can used for
Along time not less than 10 years .
C: A Tank fill line 2.5 inch instantaneous coupling .
5.Petrol tank :
200-300 liter gasoline .
6. Electric system :
A: 2 Batteries 12V . ( 135- 165 A)
B: All electrical system made from good insulated material .
C: Provided with two head lights & two back lights .
D: Provided with front vogue & side light .
7. Additional fire equipment :
A: Monitor for water on top of the vehical could be rotated 360 . the monitor Nozzle is provided with a 2000 L / min .
B: 1100/ 20 or 1200/20 tire size ..
C: (1) Project or ( search ) light
D: (1) electronic horn with loud – speaker
E: (1) Warning light .
F: 4 Section pipe (4) inch diameter , 2.5 meter length each completed with hose eoeditors ( English thread type ) .
G: Steainer with suction basket .
H: (4) dry powder extinguisher (12) Kg .
I: Aluminized asbestos suit for entering fire (2 piece ) .
J: (80) meter rubber pipes (3/4 ) inch diameter with suitable rolls pulled .
K: Complete driver tools Kit with Jack .
L: (2) Ladders length (12) meter fitted on the top of the vehicle ( each side one ) .
M: (2) steel fine axe with unit electrical handle up to (20000 ) volts .
N: (8) rubber for fire fighting .
O: (8) fire suit for fire fighter .
P: (10) hose 20 meters long 2.5 inch instantaneous coupling .
8.Spare Parts :
Spare parts choosing by from delivery company & its enouch to maintans vehicle not less than five Years .
9. Foam :
500 Lt for each Vehicle with sent the specification for maney type of Foam .(FX or A3F)
02-06-00387 | Split unit 25 TON |  |  |  |  | 25
02-06-00388 | Freezer - 40 C0 |  |  |  |  | 30
02-06-00389 | Freezer - 120 C0 |  |  |  |  | 15
02-06-00390 | Network
| PACS (Picture Archiving and communicating system ): |  |  |  |  | 50
| state of the art and of up gradeable technology |  |  |  |  | 50
| -to serve linking the X-ray dept internally & to the following stations digitally : |  |  |  |  | 100
| conference room |  |  |  |  | 50
| operation rooms |  |  |  |  | 50
operating suite meeting room
doctor offices
microprocessor based workstation for each secretary
interface to possible tele medicine
archiving on magnetic optic disk
hard copies obtained from
laser camera
VCR (PAL)
Video printers each is connected to MRI,CT,mobile CT ,angio, DER ,digital mobile C-arm & each U/S unit
UPS
Five years maintenance incl spar parts
02-06-00391 | Main conference room |  |  |  |  | 50
Projection T.V and screen
Overhead projectors X2
Slide projectors X2
Video (pal)
Multiple X- ray viewers - mobile
02-06-00392 | Doctors offices : |  |  |  |  | 20
In each office the facility to be provided with computer terminal linked to X-ray conference room and cable of storing re- reports and pictures in digital form on discs or otherwise and supplied with a laser printer to print X-ray reports
Tow extra stations in two extra doctor offices
02-06-00393 | Pakeg unit 7,5 Ton |  |  |  |  | 700
02-06-00394 | Pakeg unit 5 Ton |  |  |  |  | 20
02-06-00395 | submersible draings Pump for spring well old model :- SP25 -15 H = 35M QFLOW = 100GPM out put connection = 3 inch flange V = 380 50HZ 3Q |  |  |  |  | 20
02-06-00396 | C02 incubator |  |  |  |  | 60
Mince - 1000 - solid state
02-06-00397 | Steam boiler 3TON |  |  |  |  | 10
02-06-00398 | Water treatment (deionized water) (hemodialysis) |  |  |  |  | 200
1-Power supply
220V power=2500W 50HZ
2-pressure supply
3 bar - 6 bar
3-out put supply
1 m3/hour - 3 m3/hour
4-equipment contain of :
A-sanfliter
B-softener (cationic)
C-culler filter
D-R-O filter
E-storage tank 2000L
F-recirculation pump
02-06-00399 | Cooling tower |  |  |  |  | 40
1-model TMC 520
2-capacity Kcal/h 1.954.000
3-number of fans 10
4-air flow M3/h 119.000
5-water flow M3/h 326
6-weight kg - Net=3.730 operating 5.930
7-number of motors 4
8-electric heater power kw 5+5
02-06-00400 | Photo graphy equipment |  |  |  |  | 50
(iron for drying the negative)
02-06-00401 | Tanks for film development |  |  |  |  | 50
02-06-00402 | BOILING PAN,GASEOUS: |  |  |  |  | 700
100LT,S/S with lid, water inlet, discharge faulet, LPG control, safety valve, jacketed, floor mounted.
02-06-00403 | BOILING PAN,ELECTRIC: |  |  |  |  | 500
As above but electric heated, controlled.
02-06-00404 | BOILING PAN, ELECTRIC: |  |  |  |  | 400
As above but steam heated, controlled.
02-06-00405 | DEEP FRYER,GASEOUS: |  |  |  |  | 600
Double well with baskets, covers, all stainless steel, ltemperature control floor mounted, size about 600x800x650.
02-06-00406 | DEEP FRYER,ELECTRIC: |  |  |  |  | 700
As above, but electric operated, 380V, 3PH,thermostatic control, timer.
02-06-00407 | COOKER, GAS RANGE: |  |  |  |  | 400
With oven, 5cuft,S/S body, burners, 900x900x800,pilot flame, controls, industrial design.
02-06-00408 | COOKER , ELECTRIC RANGE: |  |  |  |  | 450
As above but electric, thermostat control (18) KW total load, 4 hot plates, with oven.
02-06-00409 | MEAT MINCER: |  |  |  |  | 500
Heavey duty meat grinder, 1 1/2 HP motor capacity not less than 200 KG/HR, with full set of orifice plates, cutter, access.
02-06-00410 | MEAT SAW: |  |  |  |  | 500
Floor mounted S/S table and parts, 900x600mm working table, 1 1/2HP motor full protections and controls.
02-06-00411 | SLICER: |  |  |  |  | 450
Heavy-duty compact, food slicer, S/S and aluminfinish, table type, gravity feed, full set of knives and access, 1/4 HPmotor, 220V.
02-06-00412 | GRILL GASEOUS: |  |  |  |  | 400
800X500 450 high with adjustable levels, floor mounted, s/s external finish, adjustable heat of (10KW) with accessories.
02-06-00413 | GRILL ELECTRIC: |  |  |  |  | 400
AS above but electric heaters, 10KW, 380V, 3PH,controls, access.
02-06-00414 | OVEN, GASEOUS: |  |  |  |  | 400
1000X800X500 depth oven, glass door, adjustable, temp, shelving, all S/S construction, accessories, timer temp. Indicator.
02-06-00415 | OVEN,ELECTRIC: |  |  |  |  | 600
AS above but electric powered 15KW, 380V, 3PH.
02-06-00416 | FOOD CUTTER: |  |  |  |  | 500
14 bowl food cutter, all S/S, adjustable speed, easy clearable, with set of accessories, attachments spare knives, table mounted.
02-06-00417 | FOOD MIXING MACHINE: |  |  |  |  | 500
Floor mounted, 1/3hp, 1-pH motor, adjustable speed, mixing BOW1 20-quart, with full set of attachment, meat chopper, meat slicer, timer, and accessories.
02-06-00418 | KETTLE ELECTRICAL: |  |  |  |  | 600
5 LT boiling kettle, electric, controlled ,all S/S with insulated handle and base
02-06-00419 | TEA URN: |  |  |  |  | 600
20 LT electric tea earns adjustable temp. With thermostat and thermometer, level guage, all stainless steel with insulated handle and base.
02-06-00420 | POTATO PEELER: |  |  |  |  | 400
Floor mounted 8LT load, 1/2 hp motor with full accessories and attachments.
02-06-00421 | HOT CUPBOARD: |  |  |  |  | 400
1100X650X800 hight, electric heated, 50-130C,controlled, all S/S, sliding door, heated top, insulated feet.
02-06-00422 | ICE CUBE MACHINE: |  |  |  |  | 500
Chest type with storage bin, 4 KG/HR ice-making machine, S/S construction, automatic operation.
02-06-00423 | INSECT KILLER: |  |  |  |  | 1000
Hanging U.V.lamp, industrial insect killer with HV grid, collection tray.
02-06-00424 | SINK AND TABLE: |  |  |  |  | 600
Heavy guage S/S, round edges, back splash table, double BOW1, mounted on S/S.
02-06-00425 | PREPERATION TABLE: |  |  |  |  | 500
Heavy guage S/S, round edges table, mounted on S/S legs, with low grid shelf, dim 2100x650x900, wood reinfored.
02-06-00426 | MOBILE SINK: |  |  |  |  | 500
Sink (1) mm S/S, on castors, 220 LT with drain valve.
02-06-00427 | STAINLESS STEEL SHELVING: |  |  |  |  | 500
Heavy guage shelving adjustable hight of 4 shelves per unit, each 1400x550, hight 800mm post 35m spuare S/S.
02-06-00428 | CONVECTION OVEN: |  |  |  |  | 600
Electric operated, (10) shelves of 500x650mm upto 180 C, floor mounted, adjustable temp, timer, heavy duty motor/fan, glass doors, over all dim 900x900x750 on legs of 650mm high, 10 - 15KW, 380V,S/S construction, well insulted, with full accessories, 20 pans, pan carier, trolley.
02-06-00429 | Bench surface protector |  |  |  |  | 500 packets
02-06-00430 | Drying cabinet ,large |  |  |  |  | 500
02-06-00431 | Dryining rack wall mounted & bench top 72 place, 22 place |  |  |  |  | 500for each
02-06-00432 | Air condition 2.5ton |  |  |  |  | 500
02-06-00433 | Telephone exchange system |  |  |  |  | 500
200 inter line
10 outer line
02-06-00434 | Freezer, - 80C |  |  |  |  | 500
02-06-00435 | Deep freezer (-70 , -120 C ) |  |  |  |  | 500
02-06-00436 | Chilled water airconditioning system 50K.W |  |  |  |  | 500
02-06-00437 | Aircondition package type 25K.W. |  |  |  |  | 500
02-06-00438 | Window type airconditioner 24000 P.t.U |  |  |  |  | 500
02-06-00439 | Window type airconditioner 18000 P.t.U |  |  |  |  | 500
02-06-00440 | Emessioning water pump 4” |  |  |  |  | 500
02-06-00441 | Emessioning water pump 3” |  |  |  |  | 500
02-06-00442 | Freezing store room 18m3 -30”C |  |  |  |  | 500
02-06-00443 | Cold store room 24m3 - 4” C |  |  |  |  | 500
02-06-00444 | Electric hot water boiler 3000 lit3 |  |  |  |  | 500
02-06-00445 | Refrigerator 6 feet |  |  |  |  | 500
02-06-00446 | Refrigerator 12 feet |  |  |  |  | 500
02-06-00447 | Coloured T.V 16 inch |  |  |  |  | 500
02-06-00448 | Telecommunication unit 400 lines with telephones |  |  |  |  | 500
02-06-00449 | P.C. computers |  |  |  |  | 500
02-06-00450 | Mechanical & electric tools |  |  |  |  | 500sets
02-06-00451 | Flour mixer capacity 100gm |  |  |  |  | 500
02-06-00452 | Bread fertilizer |  |  |  |  | 500
02-06-00453 | Baker oven electric |  |  |  |  | 500
02-06-00454 | Meat mixer large size |  |  |  |  | 500
02-06-00455 | Electric coolr large size |  |  |  |  | 500
02-06-00456 | Pick up motor vehicle 1 ton |  |  |  |  | 500
02-06-00457 | Clothes washer machine large size |  |  |  |  | 500
02-06-00458 | Clothes steam iron machine larg size |  |  |  |  | 500
02-06-00459 | Vaccum floor dryer |  |  |  |  | 500
02-06-00460 | Hoover (vaccum cleaner) |  |  |  |  | 500
02-06-00461 | Dry woop |  |  |  |  | 500
02-06-00462 | Double trolly carrige for floor cleaning with woop & seguer with 2 plastic bags |  |  |  |  | 500
02-06-00463 | Electric table calculator |  |  |  |  | 500
02-06-00464 | Grass grinder electric |  |  |  |  | 500
02-06-00465 | Electric arabic printer |  |  |  |  | 500
02-06-00466 | Electric english printer |  |  |  |  | 500
02-06-00467 | Tool & equipment for mechanical work shop |  |  |  |  | 500set
02-06-00468 | Tool & equipment for electronic work shop |  |  |  |  | 500set
02-06-00469 | Closed circuit TV. system |  |  |  |  | 500
02-06-00470 | Cameras fixed in operation theaters with out door monitoring system |  |  |  |  | 500
02-06-00471 | Computor for hospital use |  |  |  |  | 500
02-06-00472 | Laundary & CSSD central station |  |  |  |  | 500
02-06-00473 | Bleep- Doctor call (3 miles range) |  |  |  |  | for500person
02-06-00474 | Equipment-dusters |  |  |  |  | 5000
02-06-00475 | mist spriying machine holed by back with spare parts |  |  |  |  | 5000
02-06-00476 | fogging mechine with spare parts- the A/M item should be included the followingtechnical specifications 1- self starting engine (4 storke machine ) 2- multi purposes unit cap be used for thermal foging low volume application is cold aerosol sparyer for residual treatment is larvicidespraying 3- accessorise for the control of temprerture according to the weather conditions also for regulation of the size of particls is for those of spraging 4- double spraying lances 5- adjusting value for regulation of the lange of fog generation between 400-600 m(3) /min is expenditune of 10-200 gallon/ hr 6- range of diameter of partiles 0.5-200m(micron) |  |  |  |  | 1000
02-06-00477 | trailer with spare partes |  |  |  |  | 1000
02-06-00478 | hudson x-pert 10 liter with spare partes |  |  |  |  | 2000
02-06-00479 | wheal barrow power sprayer 100 liter with spare partes |  |  |  |  | 1000
02-06-00480 | IGEPA TF 35 fog generator with spare partes |  |  |  |  | 1000
02-06-00481 | IGEPA high performance FOG generator (jumbo) with spare partes 100 |  |  |  |  | 1000
02-06-00482 | IGEPA HD 160 with spare partes |  |  |  |  | 1000
02-06-00483 | cooling tower |  |  |  |  | 10
capacity : 750 ton = 9X 10^6 Btu/hr = 2268.66 thermie /hr
water out let temp. 7-26 C0
wet bulb temp 24.5C
water flow rate = 330 m^3 /hr
tower weight empty weight : 2630 kg
full with water : 7810kg
basin capacity : 3.74 m^3
fans type propeller not exit than 3 fans for each tower
fans motor power :9kw
packege :type PVC or wood
02-06-00484 | EQUITMENT: RADIO (WIRELESS) COMMUNICATION NET WORK FOR MEDICINES CARRYING TRUCKS
CONSISTING OF THE FOLLOWING:-
- NETWORK SYSTEM OPERATE WITH CODING – DECODING DEVICE
- ALL NECESSARY ANTENNA FOR THE FOLLOWING STATIONS WITH MAST (IF REQUIRED):
CENTRAL STATION WITH DESK CONTROL AND UPS FOR 6 HOURS OPERATION:-(MULTI CHANNELS)
1. TO OPERATE ALL CHANNELS FROM ANY DESK.
2. DISPLAY FOR CODING AND DECODING SYSTEM
3. DIGITAL CLOCK
4. LAMPS FOR RECEIVING, TRANSMITTING AND STAND BY.INDUCTIA
5. SEMI-DUPLEX OPERATION (PUSH TO TRANSMIT)
| 6. RF OUTPUT POWER SUFFICIENT TO COVER AN AREA OF COUNTRY OF IRAQ. |  |  |  |  | 50
FIXED STATION (MULTI CHANNELS):
7. TO COMMENCE WITH CENTRAL STATIONS AND OTHER FIXED STATIONS..
8. RF OUT PUT POWER SUFFICIENT TO COVER ALL COUNTRY OF IRAQ
9. UPS FOR 6 HOURS OPERATION
| 10. EXTRA LAUD SPEAKER. |  |  |  |  | 100
MOBILE STATIONS
| (AS FIXED STATION ABOVE) |  |  |  |  | 500
2 YEARS WARRANTY (SPARE + MEN POWER)
3 YEARS MAINTENANCE MEN POWER ONLY TRAINING FOR 4 FROM OUR TECHNICAL STAFF FOR 3 WEEKS FREE OF CHARGE.
* SPARE PARTS LIST WITH ITEM PRICE
* FULL CATALOGS (OPERATING AND MAINTENANCE WITH CIRCUIT DIAGRAM WITH EACH UNITS).
02-06-00485 | Donor chair |  |  |  |  | 50
02-06-00486 | Tube sealer |  |  |  |  | 50
02-06-00487 | Cool box |  |  |  |  | 100
02-06-00488 | CO2 or N2O |  |  |  |  | 50 bottel
02-06-00489 | high tension switch gear
| vaccum type 11KV input - 420V out put -3ph -1600A with complete protection devise |  |  |  |  | 100
02-06-00490 | plasma deep freez |  |  |  |  | 800
02-06-00491 | portable personal dust sampler |  |  |  |  | 70
02-06-00492 | Freez -20C |  |  |  |  | 10
02-06-00493 | Steam boiler |  |  |  |  | 70
rating : 1000 kg/hr from 100 C0 feed water
desing : 3- pass wet back fire tube
burner : dual fule , LPG and light gas oil
standard : B.S 2790 and equivalent
quality :150 9001
full automatic packaged boiler with atomatic blowdown system feed water pump level control , control panal , safty fitting , valves as necessary , with :
a) dual base - exchange softener of 5 m3/hr at 220 ppm water hardness
b) 10000 lt fuel tank
c) 2000 lt condensate tank
d) blow dowen receiver complete
e)5 meters chimeny
f) chemical dosing pump with tank and fitting complete
g) 5 year recommended spare parts
h) 1 year warranty
I) training of 2 engineers in factory
j) supervision on installation
02-06-00494 | DUPLEX WATER SOFTENING PLANT |  |  |  |  | 20
SADDAM MEDICAL CITY
Supply a duplex water softener :
Service flow rate : 90m3\hr
.Ion exchange resin type : strong cation
Ion exchange resin volume: 3800 liters
Underbed : coarse and fine gravel
Operation mode : automatic / manual
Net capacity of softened water per regeneration /unit :950m3(based on 200 PPM input)
Regeneration initiation flow meter
Salt consumption per regeneration : 430 kg
Brine tank recharge capacity : 1.25m3
| Working presser |  |  | 5.0 bar max
1.72 bar min.
electricity supply : 380v,3 phase,50 Hz
fully wird,piped assembeled on skid , control panel fitted ready to connection.
full detailed specs and drawings to be submitted
| Ultraviolent water bacteria removal unit for 10 m3/hr filtered water |  |  |  |  | 30
| 10 m3/hr filter for drinking water,dublex sand filter with automatic controls flow intiated with full accessories |  |  |  |  | 30
| Set of 5-year spare parts,training,supervision on installation,test kits,consumables for one year,to be included for above. |  |  |  |  | 10Lot
02-06-00495 | NURSE CALL SYSTEMS
MANUFAC.DUKANE
SADDAM MEDICAL CITY
| SYSTEMS COMPLETE REBUILD, SUPLLY OF REPLACEMENT 100 CENTRAL NURSE STATIONS, DOOR INDICATORS,PATIENT |  |  |  |  | 10 LOT
CALL CORDS ,BUTTENS AND ACCESSORIES
| INSTALLATION,SPAREPARTS FOR 5 YEARS,TRAINING |  |  |  |  | 10 LOT
02-06-00496 | DOCTOR CALL SYSTEM
REPAIR OF
NIRA TELESTAR
Saddam Medical city
| Wireless bleep system to cover no less than 5KM radius area, central station, with 1000 pocket receiver, message LCD, rechargeable batteries and storage battery rack.With interface unit to PABX system |  |  |  |  | 10
| Set of 5-year spare parts,one year consumables,training,supervision on installation |  |  |  |  | 10 lot
3 sets of technical documents,to be included for above
02-06-00497 | Electronic master clock system |  |  |  |  | 50
saddam medical city
Electronic master clock system consists of :
1-master time center
2-solid state generator
Each hour the master time center should initiate clock correction pulse which keys the solid state generators, the solid state generators in turn provide acarrier frequency current signal which transmitted over the building power wires to the wall clocks for time correction.
Replacement to SIMPLEX CLOCK SYSTEM manufactured by SIMPLEX TIME RECORDER CO.Inc (2350 master clock, 2850 solid state generator).
Spare parts for one year operation.
| Secondary wall clocks, single face. |  |  |  |  | 200
| Secondary wall clocks, double face. |  |  |  |  | 100
| Set of 5-year spare parts.training.supervision on installation to be included for above |  |  |  |  | 5 lot
02-06-00498 | UNINTERRUPTIBLE POWER SUPPLY UPS
SADDAM MEDICAL CITY
| AC POWER STATION 1.5 KVA COMPLETE WITH BATTERIES. |  |  |  |  | 60
VOLTAGE INPUT : 220 VAC
OUTPUT : 220 VAC
FREQUENCY : 50 HZ
TRANSFER TIME : 50 – 100 MS
FULL RATED LOAD FOR 90 MINUTES MINIMUM
LOAD POWER FACTOR 0.85 LAY OR 1.0 LEAD
| Set of 5-year spare parts,training, |  |  |  |  | 5 LOT
02-06-00499 | Central Medical VACUUM PUMP
SADDAM MEDICAL CITY
| VACUUM PUM UNIT COMPLETE |  |  |  |  | 10
FREE AIR DISPLACEMENT AT ATMOSPHERIC PRESSURE 760MMHG 1350 L/MIN
VOLUMETRIC THROUGH PUT AT LINE VACUUM 4050 L/MIN, 7.5KW-MOTOR
VACUUM PUM UNIT COMPLETE
| FREE AIR DISPLACEMENT AT ATMOSPHERIC PRESSURE 760MMHG 900 L/MIN |  |  |  |  | 10
VOLUMETRIC THROUGH PUT AT LINE VACUUM 2700 L/MIN, 5KW-MOTOR
| VACUUM PUM UNIT COMPLETE |  |  |  |  | 15
FREE AIR DISPLACEMENT AT ATMOSPHERIC PRESSURE 760MMHG 6750 L/MIN
VOLUMETRIC THROUGH PUT AT LINE VACUUM 20250 L/MIN, 40KW-MOTOR
02-06-00500 | EQUIPMENT : central telephone exchange |  |  |  |  | 5
model: telecom SL-1
company / manufacturer : northern telecom
site : saddam medical city
required is to update existing system with new central PABX which should exceed original features and services using same building wiring system and same telephone sets in addition suply of
complete system components
telephone sets
TTY/PRINTERS
attendant counsels
set of 1-year consumables
set of 5-year spare parts
set of tools and accessories
factory and on sit training
02-06-00501 | equipment : steam sterilizer complete
site : saddam medical city
| 200 it steam sterilizer , multi - purpose steam jacketed stainless steel chamber , sliding door free - standing , built in steam generator , air compressor ,totally enclosed by stainless steel panels , programmable, temp - press recorder , remp , press clear indicators , with loading trolly , internal basket ready to operate after connection to water supply and 380v , 3ph, 50hz power |  |  |  |  | 30
| as above bute 500 it |  |  |  |  | 10
| ro- water treatment station to suit tow of item 1 above and one of item 2 above |  |  |  |  | 10
| recommended 5- year spare parts training supervision on installation for above |  |  |  |  | 5 lot
02-06-00502 | PUMPS COMPLETE
| QTY | power Rev | suction | discharg | capacity 1/s | head
|  | KW sec | mm | mm |  | m
| 10 | 30 48 | 100 | 75 | 16.5 | 80
| 10 | 5.5 48 | 65 | 50 | 12.5 | 35
| 10 | 10 48 | 65 | 50 | 14 | 55
| 10 | 11 48 | 65 | 50 | 10 | 65
| 10 | 0.75 24 | 50 | 37 | 4 | 10
| 10 | 18.5 24 | 150 | 100 | 56.25 | 20
| 10 | 1.1 48 | 31.25 | 25 | 3.5 | 14
| 10 | 2.25 24 | 75 | 62.5 | 8.5 | 12
| 10 | 30 24 | 150 | 125 | 28.6 | 32.8
| 10 | 0.75 24 | 56 | 50 | 3.36 | 7.5
| 10 | 2.2 24 | 86 | 50 | 5.28 | 13.5
| 10 | 7.5 24 | 100 | 65 | 15 | 25.5
| 10 | 4 24 | 125 | 100 | 17.42 | 11
| 10 | 2 0.25 | 40 | 40 | 1.5 | 3
| 10 | 4 16 | 125 | 125 | 22.5 | 9.8
| 10 | 3 16 | 125 | 125 | 12.5 | 9.8
| 10 | 2.2 48 | 50 | 50 | - | -
| 10 | 0.75 24 | 65 | 65 | 3.22 | 7
| 10 | 1.1 24 | 65 | 40 | 3 | 11
| 10 | 2.2 24 | 80 | 50 | 4 | 12
| 10 | 1.5 24 | 80 | 50 | 5 | 11
| 10 | 2.2 24 | 80 | 50 | 7 | 12
| 10 | 2.2 24 | 80 | 50 | 8 | 12
| 40 | 4 48 | _ | 75 | 5 | 20
| 20 | 8 48 | _ | 100 | 6 | 20
| 40 | 2 48 | _ | 50 | 4.2 | 20
02-06-00503 | BATTERIES
Saddam Medical city
| Nickel cadmium battery block ,24vdc,280AH,shipped dry with sufficient quantity of electrolyte ,suitable for standby generator starter |  |  |  |  | 30
| As above but 110vdc,100ah,suitable for electrical switchgears |  |  |  |  | 25
Kitchen equipment
saddam medical city
02-06-00504 | Boiling pan,electric: |  |  |  |  | 60
100 Lt , s/s with water inlet , discharge faucet , LPG control safty valve , jackted , floor mounted , electric heated, controlled with all accessories and spare parts for one year operation
02-06-00505 | Boiling pan, steam : |  |  |  |  | 10
As above but steam heated, controlled, with all accessories and spare parts for one year operation.
02-06-00506 | deep fryer electric |  |  |  |  | 40
Double well with baskets, covers, all s/s , temperature control, floor mounted, dimensions approx. 600*800*650
electric operated , 380 V /50 hz /3ph, thermostatic control , timer
, with all accessories and spare parts for one year operation.
02-06-00507 | Cooker, electric range : |  |  |  |  | 10
With oven, 5 ft3, s/s body, burners, dim. Approx. 900*900*800, pilot flame, controls, industrial design.
electric , thermostat control , (18 )kw total load , 4 hot plates
With all accessories and spare parts for one year operation.
02-06-00508 | Meat mincer : |  |  |  |  | 15
Heavy duty meat grinder, 1.5 Hp motor capacity, not less than 200Kg/Hr, With all accessories and spare parts for one year operation.
02-06-00509 | Meat saw : |  |  |  |  | 10
Floor mounted, s/s table and parts, dim. Approx.900*600mm working table, 1.5 Hp motor, full protections and controls, With all accessories and spare parts for one year operation.
02-06-00510 | Slicer : |  |  |  |  | 5
Heavy-duty compact food Slicer, s/s and aluminum finish table type, gravity feed, 0.25 Hp motor, 220V. With all accessories and spare parts for one year operation.
02-06-00511 | Grill, gaseous : |  |  |  |  | 30
Approx. Dim. 800*500*450, with adjustable levels, floor mounted s/s external finish, adjustable heat of (10) kW, With all accessories and spare parts for one year operation.
02-06-00512 | Oven, gaseous : |  |  |  |  | 40
Approx. dim. 1000*800*600 depth oven, glass door, adjustable temp., shelving, all s/s construction,temp. indicator, timer, With all accessories and spare parts for one year operation.
02-06-00513 | Oven, electric : |  |  |  |  | 15
As above but electric powered, 15kw,380V/50Hz/3Ph.
02-06-00514 | Food cutter : |  |  |  |  | 10
14” bowl, food cutter, all s/s, adjustable speed, easy cleanable, table mounted, With all accessories, attachments and spare parts for one year operation.
02-06-00515 | Food mixing machine : |  |  |  |  | 10
Floor mounted, 1/3 Hp, 1-pH motor, adjustable speed, mixing bowl 20 quart, with full set of attachment, meat chopper,and meat slicer,. , With all accessories and spare parts for one year operation.
02-06-00516 | Kettle electrical |  |  |  |  | 40
5-LT boiling kettle, controlled, all s/s with insulated handles and base. With all accessories and spare parts for one year operation.
02-06-00517 | Tea urn : |  |  |  |  | 25
20-LT electric tea urn, adjustable temp. with thermostat and thermometer, level gauge, all s/s, with insulated handles and base. With all accessories and spare parts for one year operation.
02-06-00518 | Potato peeler : |  |  |  |  | 10
Floor mounted, 8-LT load, 1/2Hpmotor, with all attachments, With all accessories and spare parts for one year operation.
02-06-00519 | Hot cupboard : |  |  |  |  | 15
110*650*800 height, electric heated, 50-130 C, controlled, all s/s, sliding doors, heated top, insulated feet. With all accessories and spare parts for one year operation.
02-06-00520 | Ice cube machine : |  |  |  |  | 70
Chest type with storage bin, 2kg/hr, ice making machine,all s/s, automatic operation, With all accessories and spare parts for one year operation.
02-06-00521 | Insect killer : |  |  |  |  | 60
Hanging U.V. lamp, industrial insect killer with HV grid, collection tray, With all accessories and spare parts for one-year operation.
02-06-00522 | Sink and table : |  |  |  |  | 15
Heavy gauge s/s, round edges back splash able double bowl mounted on s/s approx dim : 2100x650x900 with all accessories and spare parts for one year operation
02-06-00523 | Preparation table : |  |  |  |  | 10
Heavy gauge s/s, round edges table, mounted on s/s legs, with low grid shelf, dim.:2100*650*900, wood reinforced.
With all accessories and spare parts for 1- year operation.
02-06-00524 | Mobile sink : |  |  |  |  | 15
Sink (1)meter s/s, on castors, 220 LT with drain valve. With all accessories and spare parts for one year operation.
02-06-00525 | Stainless steel shelving : |  |  |  |  | 15
Heavy gauge shelving adjustable height of 4-shelves per unit dims. 1400*550*800 height, post 35mm2 s/s
02-06-00526 | Convection oven : |  |  |  |  | 15
Electric operated, (10)shelves of 500*650mm up to 180C, floor mounted, adjustable temp., timer, heavy duty motor/fan, glass doors, over all dim. 900*900*750 on legs of 650 mm height, 10-15 kW, 380v, s/s construction, well insulated, with 20 pans, pan carrier and trolley, With all accessories and spare parts for one year operation.
02-06-00527 | Medium voltage switchgear
saddam Medical city
| Type |  |  | Closing voltage | Tripping voltage
| Air circuit breaker AH-40C |  |  | 220vac | 24vdc | 15
| Air circuit breaker AH-50C |  |  | 220vac | 24vdc | 15
| Air circuit breaker AH-40C |  |  | 220vac | 24vdc | 10
| Air circuit breaker AH-30C |  |  | 220vac | 220vdc | 10
| Air circuit breaker AH-30C |  |  | 220vac | 24vdc | 15
| Air circuit breaker AH-30C |  |  | 220vac | 24vdc | 10
The offer should include the following accessories:
1-tester type OCR ANH-1B, qty:1
2-tester type ANR-1 portable checker, qty:1
3-JWB-6 lifter loader (HB)AH50C/60C 3P, qty:1
4-JWB-O-H loader for AH50C, qty:1
5-JWB-O B34 loader for AH40C 4P, qty:2
6-JWB B33 loader, qty:2
7-JWB-O-M extension rail, qty:4
8-JWB-O-P extension rail, qty:1
Offer should include training of 2-engineer for 2-weeks.
Offer should include original catalogues for operation and maintenance of circuit breakers and checkers.
Vehicles
saddamMedical city
02-06-00528 | Passengers intercity staff bus .40 to 50 passengers,automatic doors ,diesel engine,air condtioned,apholestered chairs stainless steele fram,sliding glass windows with curtains,rubber mat floor, tinted windshield , stereo radio-recorder,ceiling hanging grips, |  |  |  |  | 100
02-06-00529 | Passegers staff mini bus 20-30 persons ,and as above |  |  |  |  | 100
02-06-00530 | Fire fighting vehicle.turntable telescopic up to 30 meters ladder with rescue cage, with adjustable fire hose and jet,fully equiped for fire fighting ,rescue and maintenance tasks,non skid platforms,flood and spot light projectors, |  |  |  |  | 20
02-06-00531 | Fire fighting water tank vehicle of 13000 lt ,with pump 1000lt/min at 10bars,diesel engine with accessories |  |  |  |  | 20
02-06-00532 | Mini excavator of 1 meter width 30 liters bucket,less than 25hp engine,hydraulic system, closed glass canopy,heavy rubber tracking chain,with concrete digging attachment,full accessories. |  |  |  |  | 20
| 5-year spare parts,inspection befor e contracting ,training on repair and maintenance in the manufacturers workshops.for 2 engineers on above items |  |  |  |  | 10 Lot
EQUIPMENT: SUB – STATION
SADDAM MEDICAL CITY
02-06-00533 | STEPDOWN TRANSFORMER DELTA/ STAR 11000/400VOLT, 3500KVA, 50HZ,DRY TYPE,fitted in aventilated enclosure with proper degree of protection capaple of carrying 15% contineous over load with list of 5-years spar e parts and accessories |  |  |  |  | 10
02-06-00534 | high-voltage switch gear 3-individual panels containing 3-horizontal draw out C.B(630AMP) systm voitage 11KV , 3phase , 3wire , 50HZ with all necessary monitoring and brotection devises, also 110Vdc charger shall be included 5-years spare part shall be included qty 1 complete CB with other recommended spare part. the C.B.S shall be electrically operated and manually in emergency case |  |  |  |  | 6
02-06-00535 | MEDIUM VOLTAGE SWITCH BORD shall consist of following: qty:3-incomming feeder-5000A qty:2-tie breaker . 5000A qty:9-chiller feeder. 1600A qty:1-dummy panel five years spare parts shall include qty:2 C.B 1600AMP and qty 1 C.B 5000AMP and other recommended spare parts the main and tie C.B.S shall be manually and electrically operated with all protection and metering devices |  |  |  |  | 2
02-06-00536 | BUSWAYS 5000 AMP. RATING |  |  |  |  | 160meters
totally enclosed water proof low impedance busways between transformers secondaries and M.V main switch board,completd with hanging devices aksessoris.specal tools 5-years spar parts
02-06-00537 | BUSWAYS, 1600 AMP. RATING. |  |  |  |  | 750 meters
AS ABOVE BUT BETWEEN MAIN SWITCH BORD NAD the CHILLERS
the following conditions shall be prouided for all above items a-installation , commissioning and 1-year guarantee after commissioning b-the equipmant shall operate at 50C ambient temp C-full set of detailed clear and original catalogues d-training of 3-engineers for 3-weeks in manufacturer companies
02-06-00538 | PUMPS WITH MOTORS
380 V/ 3PH/ 50HZ,TYPE SPLASH PROOF MOTOR
SADDAM MEDICAL CITY
| MODEL | KW | HEAD (M) | FLOW (L/S) | RPM
| 12LN21 | 340 | 36 | 650 | 1440 | 12
| 12LN17 | 265 | 52. 5 | 335 | 1440 | 20
| 12LN17 | 224 | 36 | 372 | 1440 | 8
| ERP80-400 | 150 | 140 | 30 | 2880 | 4
| 12LA2 | 150 | 25. 5 | 415 | 1440 | 4
| 12LA2 | 90 | 30 | 300 | 1440 | 6
| 10LA3 | 90 | 30 | 170 | 1440 | 4
| 10LA3 | 90 | 43. 3 | 142. 3 | 1440 | 4
| 65WP315 | 75 | 132. 5 | 22. 5 | 2880 | 4
| 6L3 | 55 | 32 | 101. 29 | 1440 | 4
| 6L3 | 55 | 52. 5 | 52. 24 | 1440 | 4
| 65WP315 | 55 | 103 | 22. 5 | 2880 | 6
| ERP60-200 | 45 | 190 | 7. 57 | 2880 | 12
| 50wp315 | 37 | 103 | 10 | 2880 | 6
| 65WP250 | 37 | 68. 6 | 22. 5 | 2880 | 6
| 6L3 | 37 | 34 | 55. 5 | 1440 | 6
| 6L3 | 30 | 27 | 98. 5 | 1440 | 4
| 100WP200 | 30 | 37 | 43. 1 | 2880 | 4
| 80WP160 | 15 | 24 | 30 | 2880 | 4
| 1 ½ TM2 | 15 | 132. 5 | 2. 5 | 2880 | 2
| 40WP200 | 11 | 45 | 7. 57 | 2880 | 4
| 40WP200 | 11 | 55 | 4. 36 | 2880 | 4
| 1 ¼ TM43 | 7. 5 | 68. 6 | 2. 25 | 2880 | 2
| 4L1 | 5. 5 | 9 | 30. 61 | 1440 | 4
| 100WP 200 | 4 | 11 | 17. 42 | 1440 | 4
| 1 ¼ TM22 | 4 | 83. 3 | 1 | 2880 | 6
| 3L1 | 3 | 8 | 15. 86 | 1440 | 4
| 3dv2 | 3 | - | - | 2880 | 4
| 32wp160 | 1.5 | 14.6 | 2.25 | 2880 | 4
02-06-00539 | equipment : air compreesor |  |  |  |  | 30
trolly units attas capco
tank capacity 20 litter
model of comp. : LXF 06
motor : 1 ph, 50 hz, 220 v , 0.55 kw
02-06-00540 | equipment : electric distribution
| C.B type SACE,50HZ, 3PH, 660V,1600A |  |  |  |  | 20
| C.B type SACE,50HZ, 3PH, 660V,1250A |  |  |  |  | 30
| C.B type SACE,50HZ, 3PH, 660V,630A Awith motor |  |  |  |  | 50
| C.B type BBC 600,50HZ,1PH,(250-380)V,32A |  |  |  |  | 800
| C.B type BBC 600,50HZ,1PH,(250-380)V,10A |  |  |  |  | 800
| LIP-Air C.B 600V,1600A |  |  |  |  | 25
| MCCB,3P,(380-400)V,H,1600A |  |  |  |  | 50
| MCCB,3P,(380-400)V,H,1250A |  |  |  |  | 20
| MCCB,3P,(380-400)V,H,1000A |  |  |  |  | 50
| MCCB,3P,(380-400)V,H,800A |  |  |  |  | 20
| MCCB,3P,(380-400)V,H,600A |  |  |  |  | 40
| MCCB,3P,(380-400)V,H,500A |  |  |  |  | 15
| MCCB,3P,(380-400)V,H,400A |  |  |  |  | 50
| MCCB,3P,(380-400)V,H,350A |  |  |  |  | 15
| MCCB,3P,(380-400)V,H,250A |  |  |  |  | 500
| MCCB,3P,(380-400)V,H,225A |  |  |  |  | 100
| MCCB,3P,(380-400)V,H,200A |  |  |  |  | 250
| MCCB,3P,(380-400)V,H,175A |  |  |  |  | 150
| MCCB,3P,(380-400)V,H150A |  |  |  |  | 60
| MCCB,3P,(380-400)V,H,125A |  |  |  |  | 60
| MCCB,3P,(380-400)V,H,100A |  |  |  |  | 250
| MCCB,3P,(380-400)V,H,80A |  |  |  |  | 100
| MCCB,3P,(380-400)V,H,75A |  |  |  |  | 70
| MCCB,3P,(380-400)V,H,63A |  |  |  |  | 150
| MCCB,3P,(380-400)V,H,50A |  |  |  |  | 120
| MCCB,3P,(380-400)V,H,30A |  |  |  |  | 250
| MCCB,3P,(380-400)V,H,20A |  |  |  |  | 150
| MCCB,3P,(380-400)V,H,15A |  |  |  |  | 150
| ELB-GR-50-2P 220V 30A |  |  |  |  | 70
| ELB-GR-50-2P 220V 20A |  |  |  |  | 70
| ELB-GR-50-2P 220V 15A |  |  |  |  | 70
| ELB-GR-50-2P 220V 150A |  |  |  |  | 70
| MCCB 1P 220V 15A |  |  |  |  | 450
| MCCB 4P (220-380)V 400A |  |  |  |  | 70
| MCCB 4P (220-380)V 225A |  |  |  |  | 70
| MCCB 4P (220-380)V 100A |  |  |  |  | 70
| MCCB 4P (220-380)V 50A |  |  |  |  | 70
| MCCB with aux.contact and alarm contact 380V 3P 5A |  |  |  |  | 70
| as above 30A |  |  |  |  | 70
| as above 15A |  |  |  |  | 70
| as above bot 220V 2P 150A |  |  |  |  | 70
| free fuse C.B 380V wall mounted 1000A |  |  |  |  | 15
| complete star-Delta control for motor 7.5HP with air compressor 5HP |  |  |  |  | 15
| complete star-Delta motor control 100KW |  |  |  |  | 10
| complete star-Delta motor control 50KW |  |  |  |  | 10
| complete star-Delta motor control 40KW |  |  |  |  | 10
| complete star-Delta motor control 20KW |  |  |  |  | 12
| complete direct on line single stage motor starting |  |  |  |  | 5
| MCCB single phase-50A |  |  |  |  | 5
| MCCB single phase-30A |  |  |  |  | 10
| MCCB single phase-10A |  |  |  |  | 5
| H-VAC-vacum C.B HT 12KV 600A |  |  |  |  | 10
| main switch 220V 30A |  |  |  |  | 50
| main switch 380V 60A |  |  |  |  | 50
| main switch 220V 100A |  |  |  |  | 50
| main switch 220V 150A |  |  |  |  | 50
02-06-00541 | magnifier |  |  |  |  | 5
02-06-00542 | iron (fordrying the negatives |  |  |  |  | 5
photo graphy
02-06-00543 | tanks for film development |  |  |  |  | 10
02-06-00544 | pumps
| type |  | KW | Q m^3/hr | H / m | r.p.m | dic cm | suction cm | Qty
| condenser pump / horizntal |  | 11 | 102 | 22.5 | 1430 | 18cm | 11cm | 10
| chiller pump / horizntal |  | 14 | 81.7 | 33 | 1430 | 18cm | 11cm | 10
| sanitery pump for 30m head / horizntal |  | 11 | 100 | 30 | 1435 | 120cm | 8cm | 10
02-06-00545 | Boiler |  |  |  |  | 10
sapcabloc press 3G
N-307447 / type 418m / 220-380V / 50HZ / 2-3KVA / 23/45 - 100KG/h/ 273 / 534 - 1186KW combust - fuel max visc 20c / 6mm^3/s (1.5E) / 1979
02-06-00546 | inter com system withall accissorice |  |  |  |  | 10
02-06-00547 | Wall clock with seconds indicator |  |  |  |  | 10
02-06-00548 | taelephone-intercom |  |  |  |  | 10
02-06-00549 | Air compresser |  |  |  |  | 50
compressor with tank
400L/M - 7Kg/cm^2
3.7KW 3Q 380V
air tank capacity :-129 liter
one work other stand by - alternative working
ins tallation for system
spare part for 5 years
training for staff
catalog for mainterance and operation and installation
02-06-00550 | Medical oxygen units |  |  |  |  | 10
1-compressor
2-air seperation unit + msun
3-stiriling cryogenerator
4-500 liter storage vessel with level control
5-super charger with clyinder filling machine up to 150PSI
6-fully automatic start and stop
7-at least 10/minute start up
8-lowest energy consumption
9-low noise level
10-automatic restart after power failar
11-cooling systemwater (cooling tower) with softner or by chiller
12-warking machine at ambient tempretuer (50-65)c
13-impurity at least 99.5% medical use
14-produces at least (50liter lequid to70)/hour.
02-06-00551 | condensor water pump |  |  |  |  | 10
400V 1500r.P.m 3Q 6"X6"
02-06-00552 | Mini bus |  |  |  |  | 1000
passanger shaft mini bus 10-20 person
gasolen engine air conditioning and heating
power steern manual gear with floor shift
two doors on the front,one in each side with middle door in the right sid
all around window ,each side window is double and slading
two view mirror in eacg side and one internal
radio and cassete recorder
all execary should be heavey duty
spare part for tow years
02-06-00553 | Motor cycle |  |  |  |  | 1000
Petrol Engine
Suitable size
Capacity of carrying:- Two persons.
Equipped with full accessories
Warranty & Maintenance for 2 years
Lest of spare part for 2 years
Training for 3 technicians
02-06-00554 | Motor cycle with side vehicle |  |  |  |  | 1000
Petrol Engine
Suitable size
Capacity of carrying:- Three persons.
Equipped with full accessories
Warranty & Maintenance for 2 years
Lest of spare part for 2 years
Training for 3 technicians
02-06-00555 | garbage collection vehicle |  |  |  |  | 250
1) basic vehicle
1- type : forward control
2- drive 4X2
3- engine : diesel engine water cooled
4- electrical equipment : 24 v 12vX2batteries 120 Ah at 20 hr
5- transmission : manual power assist
6- clutch : hydraulic control , singl dry plate with air pressure assistance
7- tires :single front dual rear
8- steering :left hand steering ball mute type with integral type hydraulic power booster telescopic and tilt steering column with steering lock
9- front suspensions : laminated leaf springs with shock absorbers
10- rear suspensions : laminated leaf springs
11- front :parallel tapered channel section type with crossmember and reinforcements
12- fuel tank :250 liters
13- drivers cab : all steel titl cab equipped with A/C
14- paint : finish coat crystal white
15- measurement : metric (km/h)
16- brakes : service :air over hydraulic with dvel circuit
parking : internal expanding type on propeller shift
auxiliary : exhaust brake
17- cooling system :radiator : corrugated fin type with pressure cap and surge tank
fan: multi- blades steel
18- Caution Plate : Arabic
2) garbage container
1- container volume : (12-16) m3
2- contanier structure :suitable steel or metal
3- loading mechanism :- hydraulically controlled mechanical press type
4- with full accessories for all vehicle & container
*training for three technicians
* warranty & maintenance for tow years
*lest of spare part for 2 years
02-06-00556 | Eleveters
1-technical opecifications
a-full electronic control sistem for operation and level selection conteining all necessery equipments for protection and supervision
b-type of control 3V -3F,elevater continioys speed : (0.5-2.5) M/sec-adjustable according to capacity and number of levels
c-door opnning : automatic and swing according to the site biulding
d-emergency power supply (ups) providing necessry electric power at least for stopping the carriege at nearest level as well as the control system contain back up batteries for saving stored data for at least 1000 hours
e-ambient tempreture 0-50C and 90% hum
f-the system contain data terminal (pc-bored)for operation maintenance, diognosis ,reed proqrams and reprograming,with probability to remote maintenanct
g-the system contain (4)four stopping stages at final up and final down
h-the carrieg modle from stainless-steel with smooth surface,painted with standard coulor with non -slipery platform,containing emergency lighting and ventilation,with communication limk between the systen and to the telphone exchange,also contain at T.system
2-installation equipments on sites with all accesseries.
3-one year warranty and two years maintenance after period of warranty .
4-fraining on factoru for 6-technical staff x 3weeks and local traing during installuation
5-spare parts for 5 years
6-quantities as per schedule.
| type | 180 kg | 500 kg | 750 kg | 1000 kg | 1200 kg | 1600 kg | 2000 kg
| passenger | _ | 90 | 90 | 80 | _ | _ | _
| bed lift | _ | _ | _ | _ | 90 | 100 | 90
| service | 20 | _ | 50 | _ | _ | _ | 50 hydrolic
02-06-00557 | Medical oxygen plant |  |  |  |  | 200
_ complet liquid oxygen production plant
capacity: 75LIT.liquid/hour
purity :not less than 99.5%
(including an electrical analyzer on line)
air compressor type
_ oil free
_ reciprocating
_ suction temp. (50-60)c
_ low pressure
storage and filling station
_ one liquid storage tank (capacity:10000lits)
_ complete common cylinder filling plant with dual charging manifold (5-10 cylinders each)
including the following (for each plant)
_ 2sets of instruction manuals operation and maintenanece
_ 2sets of spare parts catalogues
_ 2set of special tools
spare parts
spare parts for five years operation as recommened by the manufacturer
guarantee
12 months from the date of start up
training
trining of two technicians during four weeks at the factory
02-06-00558 | POWER SUPPLY
U.P.S
steady 220Vout put voltage, with NICD or sealed acid baheries, duration time 30 min for 60 KVA , 180 min for others
| 1KVA |  |  |  |  | 100
| 2 KVA |  |  |  |  | 100
| 3 KVA |  |  |  |  | 60
| 5 KVA |  |  |  |  | 150
| 10 KVA |  |  |  |  | 60
| 60KVA |  |  |  |  | 40
02-06-00559 | cooling for operating room
Air conditining equipment for operating theaters as following
Cooling capacity
1- air conditining system is working with 100% fresh air
2- requried room conditions
room temperature 20-25 Co
relative humidity 45-60 % r.h
3- ambient temp 60 Co
4- cooling and heating
5- heating electric heater direct without hot water boilers
air condtioning plant mainly consisty at
1- air cooled condensor
2- cold water pumps
3-exaust air handing unit
4-of supply air ceiling system with high efficiency filter high type (s) with:
a- filter ceiling air outlet with high efficiency filter type (s)
b- control and regulation system
c- steam humidifier filter class (b) ,c sound absorber for supply and exhaust air duct system with nessary insulation air tight damper tight grill weather proof louvers cold water lines with insulation and electric cable and any other part for the system
6-spare parts for five years
7- training for 3 engineer in the manufacturer factory
| capacity |  |  |  |  | qty
| 2 ton |  |  |  |  | 60
| 5 ton |  |  |  |  | 120
| 10 ton |  |  |  |  | 60
| 15 ton |  |  |  |  | 20
| 20 ton |  |  |  |  | 60
| 30 ton |  |  |  |  | 4
02-06-00560 | digital ISDN network |  |  |  |  | 5
* the system consist of following no. central station (exchange) 500 port no. 14 branch station (exchange ) extandable to 30 each branch 120 ports
* the communication way between the control station and the branches either VIA PTT or by micro wave form
* the system able to be connected with fier alarm system and security system (prefer to be including with the offer ) and air conditioning system or any other system in the branch sites
* istallation including all necessory accissories
* warrenty one year from operation time
maintenance tow years after period of warrenty
* spare parts for 3 years
* traning on factory of equipment and local training during installation
02-06-00561 | specification of fire fighting system (automatic - sprinkler system)
design manfacutre diliver and installation of an automatic roop sprinklers system in the warehouse in different sites including the following equipment persite
site specification :-
| 1- effective warehouse area 8000 m2 , height 10m |  |  |  |  | 15
| 2- effective warehouse area 12500m2 , height 6m |  |  |  |  | 10
| 3- effective warehouse area 2000 m2 , height 4.5m |  |  |  |  | 20
| 4- effective warehouse area 2500 m2 , height 11m |  |  |  |  | 10
| 5- effective warehouse area 10000 m2 , height 5m |  |  |  |  | 10
| 6- effective warehouse area 25000 m2 , height 14m |  |  |  |  | 10
| 7- effective warehouse area 20000 m2 , height 8m |  |  |  |  | 10
the equipment requirement
a- all necessory pipe work fitting hanger and sprinkler heads
b- all necessory installation controlling valve and ander ground main to connect to the water storge tank
c- pump house complete with pipe work including valves and fittings
d- three automatic fire pumps two electrical and one diesel driven each rated at 3600 dm3/min at 8.5 bars
e- one culindrical galvanised steel water storge tank with an effective capacity
f- an electrically operated and pully automatic jockey pump
g- complete electrical control boards
h- eight pir exitination and fir caben with hose
I- spare parts for 3 years
j- warrnty one year ( label + material) and two year mantinance
k- training of factory of equipment for 3 technicians
02-06-00562 | transformer
| 1000 kva , 11 kv/380 v , 2500a, delta /star , 50 hz , oil cooling |  |  |  |  | 40
| 2000 kva , 11 kv/380 v , 2500a, delta /star , 50 hz , oil cooling |  |  |  |  | 40
| 630 kva , 11 kv /400v-240v, delta/star, 50 hz ,oil cooling |  |  |  |  | 40
| 360 kva , 11kv / 400-240v, delta/star ,50hz , oil cooling |  |  |  |  | 40
pumps
| pump use | head m | q l/min | size | kw | volt | type | no
02-06-00563 | fire pump /fp1 | 90 | 750 | 100 | 22 | 380 | centrifugal pump | 48
02-06-00564 | lift pump /lp1 | 50 | 1400 | 125 | 22 | 380 | centrifugal singal suction | 48
02-06-00565 | lift pump /lp2 | 25 | 750 | 50 | 5.5 | 380 | singal suction volut pump | 48
02-06-00566 | chilled water pump p-2 | 20 | 6150 | 20x150 | 30 | 380 | centrifugal pump | 48
02-06-00567 | chiller water /p-3 | 38 | 2320 | 125x100 | 30 | 380 | centrifugal pump | 48
02-06-00568 | chiller water /p-4 | 38 | 4980 | 200x150 | 45 | 380 | centrifugal pump | 48
02-06-00569 | chiller water /p-5 | 47 | 4520 | 150x125 | 55 | 380 | centrifugal pump | 48
02-06-00570 | condensor water pump p-1 | 20 | 7580 | 200x150 | 37 | 380 | centrifugal pump | 48
02-06-00571 | softener pump p-11 | 25 | 160 | 40 | 2.2 | 380 | in line pump | 48
02-06-00572 | lift pump p-12 | 55 | 100 | 40 | 3.7 | 380 | singal suction | 48
02-06-00573 | make up water pump p-13 | 15 | 180 | 40 p2 | 1.5 | 380 | centrifugal pump | 48
02-06-00574 | condensor water pump p-14 | 15 | 70 | 65x40 | 1.5 | 380 | centrifugal pump | 48
02-06-00575 | circulation hot water pump p-6 | 10 | 1410 | 100x50 | 3.7 | 380 | centrifugal pump | 48
02-06-00576 | circulation hot water pump p-7 | 37 | 480 | 65x4 | 5.5 | 380 | multy stage centrifugal | 92
02-06-00577 | circulation hot water pump p8 | 36 | 1250 | 125x2 | 15 | 380 | multy stage centrifugal | 92
02-06-00578 | circulation hot water pump p-9 | 45 | 1100 | 100x3 | 15 | 380 | multy stage centrifugal | 92
1-give complete catalag for the pump
2- 5 years spare part
3-training for the staff
4-grante for one year operation
5-installation for one site.
6-the meal of the pump must be suitable to have long lifte with the type of water which we ane using (high hardness) (TH500ppm) and easy for maintcuauce
02-06-00579 | softener pump
| kw | r.p.m | Q L/S | Hm | QTY
| 2.2 | 1500 | 5.5 | 15 | 50
| 5.5 | 1500 | 20 | 25 | 50
02-06-00580 | water pump for tower
| kw | r.p.m | Q L/S | Hm | QTY
| 2.2 | 1500 | 7.5 | 12 | 70
| 7.5 | 1500 | 16 | 27 | 50
| 15 | 1500 | 33 | 25 | 50
| 37 | 1500 | 108 | 23 | 50
| 22 | 1500 | 75 | 20 | 60
02-06-00581 | boiler feeding pump
| kw | r.p.m | Q L/S | Hm | QTY
| 5.5 | 3000 | 16.6 | 80 | 300
| 4.5 | 3000 | 6 | 13 | 100
02-06-00582 | chemical dosing pump/ with 500 litter tank and mixer variable flow and pulses
| kw | r.p.m | Q L/S | Hm | QTY
| 0.3 | 1500 | 5 | 60 | 100
02-06-00583 | horizantal pump
| kw | r.p.m | Q L/S | Hm | QTY
| 1.1 | 1500 | 2 | 15 | 100
| 5.5 | 3000 | 15 | 60 | 100
02-06-00584 | vertical pump
| kw | r.p.m | Q L/S | Hm | QTY
| 2.2 | 3000 | 7 | 50 | 100
| 4 | 3000 | 3 | 85 | 100
02-06-00585 | circulation pump
| kw | r.p.m | Q L/S | Hm | QTY
| 2.2 | 1500 | 5.5 | 25 | 300
| 5 | 3000 | 3 | 8m (hot water) | 50
02-06-00586 | submersible pump
| kw | r.p.m | Q L/S | Hm | QTY
| 3 | 3000 | 3.5 | 15 | 300
| 7.5 | 1500 | 20 | 15 | 300
| 22.5 | 3000 | 125 | 13 | 100
02-06-00587 | fire pump
| kw | r.p.m | Q L/S | Hm | QTY
| 0.75 | 3000 | 1.5 | 60 | 100
| 5.5 | 1500 | 21 | 35 | 300
| 37 | 3000 | 33 | 66 | 100
02-06-00588 | water pump for heating
| kw | r.p.m | Q L/S | Hm | QTY
| 2.2 | 1500 | 12 | 21 | 100
| 5.5 | 1500 | 10 | 25 | 100
| 7.5 | 1500 | 82 | 15 | 100
| 11 | 1500 | 28 | 22 | 100
| 15 | 1500 | 18 | 45 | 100
| 18.5 | 1500 | 36 | 33 | 100
ware house requierment
02-06-00589 | folding end trolleys capacity 150 kg |  |  |  |  | 200
02-06-00590 | manual and electrictric stackers capacity 250 kg |  |  |  |  | 40
02-06-00591 | folding work shop caranes capacity 1000 kg at 1 m |  |  |  |  | 40
02-06-00592 | cylinder trolly capacity 200 kg |  |  |  |  | 100
02-06-00593 | sterilizing water for theter room ultraviolet water purifiers |  |  |  |  | 400
Water sterilizing system to treat water for theater rooms. The system is to deliver water at a rate of 1 l/s. The system should include any pumping system required to insure adequate operation of the system, where the inlet pressure is between 0.5-1.5 bar. The price should include;
_ Installation of the system,
_ 2 years full warranty,
_ 3 years maintenance post warranty period,
_ training of professionals at the manufacturer factory (ies), and
_ Local training of staff.
The offer should include a detailed priced list of recommended spare parts for 5 years of operation, along with a schematic diagram of the system showing the location of each part.
An irrecoverable complete sample system should be delivered along with the offer.
The system should be composed of the following units;
A. A pretreatment filtration unit of (2-3) stages with the final stage of pore size less than 1μ.
B. Compact water softener (50% OF Qty).
C. UV sterilization unit with adequate power to insure efficient sterilization of water. The unit should;
_ be of stainless steal,
_ have quick lamp change,
_ have lamp life not less than 8000-10000 hours of continuous operation
_ Have UV intensity sensor and control unit with indicator light.
02-06-00594 | VEHICLE PICK-UP DOUBLE CABIN |  |  |  |  | 1000
1. PETROL ENGINE WATER COOLED
2. MANUAL GEAR BOX, FLOOR SHIFT
3. STEERING POWER STEERING LEFT HAND DRIVE
4.ELECTRICAL EQUIPMENT’S: BATTERY 12V-60AMP HEAVY DUTY
5.AIR-CONDITIONING FOR DRIVER CABIN (HEATING AND COOLING)
6. SUSPENSION: HEAVY DUTY
7. TIRES WITH TUBES: SUITABLE FOR DIFFERENT ROADS (HIGH QUALITY)
8. CABIN: SINGLE CABIN WITH DOOR IN EACH SIDE.
9. MIRRORS: TO BE EQUIPPED WITH TWO SIDES MIRRORS AND ONE INSIDE
10.ACCESSARIES: TO BE EQUIPPED WITH JACK + WHEEL WRENCH + HAZARD TRIANGLE + TOOL KITS + FAST MOVING PARTS . WITH THE VEHICLE AND ANY EQUIPMENT’S CONCERNING THE JOB OF THIS CAR.
11.LOADING CAPACITY: FROM (1-2)TONS
12.ALL MATERIALS INSERTED IN THE CONSTRUCTION OF THIS CAR IT WILL BE OF HIGH QUALITY (ROOD, SHACKLE, GOODS COVER)
13.MAINTEMANCE FOR ALL VEHICLES FOR TWO YEARS ON ACCOUNT OF THE COMPANY WITH TRAINS FOR ENGINEERS AND TECHNICIANS (5PERISON) FOR ONE MONTH
02-06-00595 | digital camera |  |  |  |  | 10
02-06-00596 | data show |  |  |  |  | 10
02-06-00597 | MCR FUMIGATOR |  |  |  |  | 16
empty wieght 7KG
diamination :- 35x32x36 cm
tention 220V
power 100watt
capacty:- 1 liter (formaldhad)
02-06-00598 | air handlig unit |  |  |  |  | 12
capaseity = 10 - 15 ton
RPM = 1500 - 3000
HP = 7 1flew rete = 30m^3/hr
No. of Row 3
heating =hot watr
type of filter = Mesh type (G.S) sheet washable
Volt = 380V / 3pH / 50HZ
02-06-00599 | air handlinunit
| capacity = 80ton heating hot watir |  |  |  |  | 12
no. of row = 3
HP=25
R.P.M =1500 - 3000
type of filter = Mesh type (G.S) sheet- washable
Volt = 380V / 3pH / 50HZ
02-06-00600 | air handlinunit
| capacity = 30ton |  |  |  |  | 12
heating =hot watr
flow rett=23000M^3/hr
No. of Row 3
HP = 15
RPM = 1500 - 3000
Volt = 380V / 3pH / 50HZ
type of filter = Mesh type (G.S) sheet- washable
02-06-00601 | capacity = 20ton |  |  |  |  | 10
HP = 7.5
heating =hot watr
No. of Row 3
R.P.M =1500 - 3000
type of filter = Mesh type (G.S) sheet- washable
Volt = 380V / 3pH / 50HZ
02-06-00602 | air handlig unit for operating theater room | [8 empty] | 10A.H.U
type / wiss technick
capasity = 50ton
heating = heater for (A and B)
A - HP = 3/10.5
flow = 2500 / 4250M^3/hr
|  | B - HP = 1.5/5.5 | [7 empty] | 10AHU
flow = 1500/ 3250 M^3/hr
R.P.M for A and B = 1500/ 3000
NO. of ROW for (A and B)=3
three type of filter for (A and B)
a -bag filter (washable
b -mesh typy (washable) G.S
C- absolute filter 99.9%
volt = 380 V/ 3 PH / 50HZ
02-06-00603 | A .H. U | [8 empty] | 25
ctm=14800ctm
HP= 8.5HP
heating=hot water
RPM= 1500/ 3000
volt = 380V / /50HZ
feltr = mesh tepe (washable)(G.S)
A .H. U
| HP | V | QTY | flow M^3/hr | type of filter
02-06-00604 | 2 | 380/3ph/50hz | 5 | 31 50 | mesh type (washable)
02-06-00605 | 7.5 | 380/3ph/50hz | 5 | 8160 | mesh type (washable)
02-06-00606 | 7.5 | 380/3ph/50hz | 5 | 9960 | mesh type (washable)
02-06-00607 | 7.5 | 380/3ph/50hz | 5 | 7990
02-06-00608 | 7.5 | 380/3ph/50hz | 5 | 8560
02-06-00609 | 3.o | 380/3ph/50hz | 5 | 3080
02-06-00610 | 7.5 | 380/3ph/50hz | 5 | 3080
02-06-00611 | 10 | 380/3ph/50hz | 5 | 7250
02-06-00612 | 7.5 | 380/3ph/50hz | 5 | 4000
02-06-00613 | 7.5 | 380/3ph/50hz | 5 | 4000
02-06-00614 | 20 | 380/3ph/50hz | 5 | 16190 | mesh type (G.S)
02-06-00615 | 7.5 | 380/3ph/50hz | 5 | 6800 | mesh type (G.S)
02-06-00616 | 7.5 | 380/3ph/50hz | 5 | 4400 | mesh type (G.S)
02-06-00617 | 40 | 380/3ph/50hz | 5 | 31700 | mesh type (G.S)
02-06-00618 | 30 | 380/3ph/50hz | 5 | 31005 | mesh type (G.S)
02-06-00619 | 25 | 380/3ph/50hz | 5 | 33030 | mesh type (G.S)
02-06-00620 | 15 | 380/3ph/50hz | 5 | 19500 | mesh type (G.S)
heating = hot water
RPM = 1500 - 3000
NO.of row = 3
02-06-00621 | FIER ALARM SYSTEM
a)specification :
1- the system should be 2- wire installation
2- the system should be able to be connected to data network or telephone exchange and recorder
3- the system should contain repeaters for stopping air condtioning and spare
4- each zone contain about 20 delectors and one glass break unit
5- the system should contain one central control and indication unit and branchs units
6- each system contain PC unit for operation and maintenance and programing if necessory
7- the detecters should be from smoke heat and temp rise type
b) quantities :
| no. of system | [8 empty] | no. of zone
| 100 | [8 empty] | 20
| 150 | [8 empty] | 40
| 100 | [8 empty] | 60
| 100 | [8 empty] | 80
| 100 | [8 empty] | 120
c)
1- one year warrenty from date of operation and tow years maintenece after period of warrenty
2- spare partes for 5- years
3- full sets of ducomants and catalogues and diagrams
4- training on factory of equipment and local training during installation
MEURO - SURGERY CENTER
LUNDRY EQUIPMENT
02-06-00622 | side loading washer 50 kg | [8 empty] | 120
02-06-00623 | centrefugal extractor 30 kg/load | [8 empty] | 80
02-06-00624 | drying tembler 25 kg/load | [8 empty] | 80
02-06-00625 | canvas truck | [8 empty] | 240
02-06-00626 | strach cooker | [8 empty] | 40
02-06-00627 | flate work ironer 50 kg/hr | [8 empty] | 80
02-06-00628 | hand ironer board | [8 empty] | 60
02-06-00629 | swing machine | [8 empty] | 80
02-06-00630 | ottlity press machine | [8 empty] | 160
02-06-00631 | electrical steam boiler 20 BHP capac. At apressure of 11kg/cm2 | [8 empty] | 40
02-06-00632 | air compressor with cylinder 0.07 m3/min capac. At apressure of 6 kg/cm2 cylinder rolame 120 l | [8 empty] | 40
02-06-00633 | disinfected washing machine | [8 empty] | 160
ELECTRICAL EQUIPMENT
02-06-00634 | high tension panal with short circuit current (25 ka) | [8 empty] | 20
02-06-00635 | high tension cable , XLPE type with (750) m length | [8 empty] | 6x150mm2
02-06-00636 | isolated transformer | [8 empty] | 24
with their control panales
| capacity (25 kva) | [8 empty] | 20
| capacity (16 kva) | [8 empty] | 20
KITCHEN EQUIPMENT
02-06-00637 | scale 1 kg | [8 empty] | 40
02-06-00638 | scale 25kg | [8 empty] | 40
02-06-00639 | scale 5 kg | [8 empty] | 40
02-06-00640 | weighing machine 100 kg | [8 empty] | 40
02-06-00641 | potata peeler 5kg /load | [8 empty] | 40
02-06-00642 | vegetable mill 300 kg /hr | [8 empty] | 80
02-06-00643 | chopping black 50x50x65 cm | [8 empty] | 80
02-06-00644 | meat mincer 2 kg /hr | [8 empty] | 80
02-06-00645 | backing oven gaseous loven 2 deck each 80x90x120cm | [8 empty] | 80
02-06-00646 | mixing machine 10 lit | [8 empty] | 80
02-06-00647 | refrigerator 420 lit | [8 empty] | 160
02-06-00648 | range gaseous (general purpose) 6 plate - 1oven | [8 empty] | 80
02-06-00649 | oven gaseous (each one of 80x90x170 cm) | [8 empty] | 80
02-06-00650 | boiling pan gaseous 35 lit | [8 empty] | 120
02-06-00651 | boiling pan gaseous 50 lit | [8 empty] | 120
02-06-00652 | gaseous fry range | [8 empty] | 80
02-06-00653 | grill gaseous | [8 empty] | 80
02-06-00654 | hot cub board | [8 empty] | 40
02-06-00655 | dish washer 640 pieces/hr | [8 empty] | 120
02-06-00656 | heated trolly | [8 empty] | 480
02-06-00657 | general purpose trolly | [8 empty] | 480
02-06-00658 | cold cup board | [8 empty] | 80
02-06-00659 | electrical water cooler 40 lit/hr | [8 empty] | 80
02-06-00660 | hood | [8 empty] | 80
02-06-00661 | bin on castors 6 kg | [8 empty] | 80
02-06-00662 | bin on castors 12.5 kg | [8 empty] | 80
02-06-00663 | bin on castors 25 kg | [8 empty] | 80
02-06-00664 | bin on castors 50 kg | [8 empty] | 80
VIDEO BEAMER
02-06-00665 | large avitoriom high lumihosity for use in light remote controlled ,complete system with link to speakers computer and monitor to accept CD rom as well | [8 empty] | 40
02-06-00666 | slide progector | [8 empty] | 160
02-06-00667 | over head projector | [8 empty] | 240
02-06-00668 | cooling tower schedule
| no req. | type | heat rejection capacity kcal/h | ambint W.B temp. C | water temp. |  | water qty. L/min | fan | electrical characteristics
[5 empty] | In | Out |  | motor kw | V | PH | HZ
| 70 | indused draft | 869400 | 26 | 35 | 30 | 2611 | 15 | 380 | 3 | 50
02-06-00669 | air washer schedual
| no. req | type | location | summer
|  |  |  | amb. Temp wb c | press. Nozzle m.w.g | water circulation lit/min
| 50 | double bank spray | block c on the roof | 26 | 25 | 750
winter (heating coil)
| grand total heat kcal/hr | air temp c |  |  |  | water temp.c |  | water qty lit/min | no of fins /25mm | no of rows
|  | in |  | out |  | in | out
|  | DB | WB | DB | WB
| 431680 | 1.5 | 0.8 | 33.5 | 5.5 | 82 | 71 | 650 | 8 | 2
| blower |  |  |  |  | circulation water pump kw | electrical characteristic |  |  | filter
| blower type | total air qty m/hr | face velocity m3/sec | total static pressure mm w g | motor kw |  | volt | phase | hertz | type | thickness mm
| centrifugal aerofoil | 121380 | 2.5 | 22 | 18 | 7.5 | 380 | 3 | 50 | metalic cleanable | 50
extractor fan
| RE NO. | location | air capacity m3/hr | no. req | pressure drop mm.w.h | input kw | electric v/ph/hz
02-06-00670 | RE-16 | A" | 1460 | 10 | 4 | 0.12 | 220/1/50
02-06-00671 | RE-17 | B | 1300 | 10 | 3 | 0.065 | 220/1/50
02-06-00672 | RE-18 | B | 12000 | 10 | 10 | 1 | 380/3/50
02-06-00673 | RE-19 | B | 3400 | 10 | 7 | 0.3 | 220/1/50
02-06-00674 | RE-20 | B | 2210 | 10 | 7 | 0.3 | 220/1/50
02-06-00675 | RE-21 | B | 1530 | 10 | 5 | 0.2 | 220/1/50
02-06-00676 | RE-22 | B | 1020 | 10 | 5 | 0.2 | 220/1/50
02-06-00677 | RE-23 | A` | 2430 | 10 | 5 | 0.5 | 220/1/50
02-06-00678 | RE-24 | A" | 1785 | 10 | 5 | 0.5 | 220/1/50
02-06-00679 | RE-25 | A" | 3100 | 10 | 5 | 0.75 | 220/1/50
02-06-00680 | RE-26 | A" | 340 | 10 | 3 | 0.3 | 220/1/50
02-06-00681 | RE-27 | A" | 1445 | 10 | 5 | 0.5 | 220/1/50
02-06-00682 | RE-28 | A" | 3215 | 10 | 5 | 0.5 | 220/1/50
02-06-00683 | RE-29 | A" | 2516 | 10 | 5 | 0.5 | 220/1/50
02-06-00684 | RE-30 | A" | 1600 | 10 | 3 | 0.3 | 220/1/50
02-06-00685 | RE-31 | A" | 1900 | 10 | 3 | 0.5 | 220/1/50
02-06-00686 | RE-32 | A" | 2265 | 10 | 3 | 0.5 | 220/1/50
02-06-00687 | RE-33 | A" | 1700 | 10 | 3 | 0.5 | 220/1/50
02-06-00688 | RE-34 | A | 1657 | 10 | 3 | 0.3 | 220/1/50
02-06-00689 | RE-35 | A`,A` | 1000 | 20 | 3 | 0.3 | 220/1/50
02-06-00690 | hood
| stainlees steel hood used for labortary to be installed above sterilizer with following dimension 1500x600 | [8 empty] | 20
02-06-00691 | water cooler | [8 empty] | 100
40 l/h cooled to 10 c
electric supply 220/1 ph/50
stainlees steel ,anti-splash top equipped with non-clogging and easy to clean integral stranier grid the tank shall be burst proof galvanized with copper refrigerator coil
02-06-00692 | window type 2 ton with heater capacity 3.6 kw | [8 empty] | 30
02-06-00693 | window type 1.5 ton with heater capacity 3 kw | [8 empty] | 30
02-06-00694 | window type 1 ton with heater capacity 2.6 kw | [8 empty] | 50
02-06-00695 | split unit 2 ton with heater capacity 3.6 kw | [8 empty] | 30
02-06-00696 | x-ray window 1.5x1.2m w/load glass | [8 empty] | 30
02-06-00697 | x-ray door fram 1.8x2.35 m w/load sheilding | [8 empty] | 30
02-06-00698 | x-ray door fram 0.9x2.1 m w/load sheilding | [8 empty] | 30
02-06-00699 | drinking water storge tank made of hot pressed steel plate of dimension (1.22x1.22) and thickness of not less than 6mm
| (7.32x4.88x2.44) m | [8 empty] | 5
| (4.88x2.44x2.44)m | [8 empty] | 5
02-06-00700 | inclarator of 300 kg /hr | [8 empty] | 5
02-06-00701 | BED HADE UINT | [8 empty] | 36UINT
each one of bed hade unit comprifing the following
| * general light 40 w with lamp | [8 empty] | 5
| * read light 20 w with lamp | [8 empty] | 5
| *cord pull switch with lamp for nurse call station | [8 empty] | 5
` | * intercom unit | [8 empty] | 5
| * doubl switch socket 13A | [8 empty] | 5
| *exam light with lamp | [8 empty] | 5
| *extra examenstion light with lamp shipt 44 seperatly | [8 empty] | 100
02-06-00702 | cold room | [8 empty] | 40
temp.: -20C to +20 C
dimention (H 2.5 m- W3 m- L3m)
cold room 2 stage unites
02-06-00703 | santiry hot water with hot pump
| power 3kw , rev 1450 sec , suction 79 mm, discharge 64mm, capacity 14 l/min , head 30m | [8 empty] | 20
02-06-00704 | SPECIFICATIONS FOR TANK TRUCK | [8 empty] | 500
( GAS OIL - CESSPOOL EMPTIER DRINKING WATER)
1) Truck Specification
1- Type : Forward control
2- Drive sys. 4 X 2
3- Loading Cap. (10.000 liters Gas oil)
( 8.000 liters cesspool emptier)
(10.000 liters drinking water)
4- Dimensions
Wheel base about 4.100 mm
Overall length about 7.535 mm
Overall width about 2.480 mm
5- Engine : Diesel engine water cooled
6- Electrical eq. : 24 Volt, 12 volt X2 Batteries, 120 Ah at 20 hr
7- Transmission : Manual Power assist
8- Clutch : Hydraulic control, single dry plate with air pressure assistance.
9- Tires : Single Front, dual rear
10- Steering : Left hand steering, Ball mute type with integral type hydraulic power booster, Telescopic and tilt steering column with steering lock.
11- Front suspensions: Laminated leaf springs with shock absorbers
12- Rear Suspensions : Laminated leaf springs
13- Front : Parallel, Tapered channel section type with cross - member and reinforcements
14- Fuel Tank : 250 liters
15- Drivers Cab : All steel, tilt cab equipped with A/C
16- Paint : Finish coat, Crystal white
17- Measurement : Metric ( Km/h)
18- Caution Plate : Arabic
19- Brakes :
Service : Air over hydraulic with dval circuit
Parking : internal expanding type on propeller shift
Auxiliary : Exhaust brake
20- Cooling system :
Radiator : corrugated fin type with pressure cap and surge tank
Fan : Multi – blades, steel
2) TANKS : Specifications
A – Gas Oil Tank
* Capacity: 10.0 KL. Gas Oil
* Type : Elliptical cross sectioned cylindrical tank
* Tank construction: tank assembly of elliptical shape, constructed with steel plate by electric welding which consists of tank shell, end plate, apparition plate, of lashing and manholes (inside 400mm dia.) each manhole cover is furnished with a filling hatch (inside 230mm Dai.) a dip stick, an air vent valve and a filling point interior surface of tank is zinc painted anti- corrosion.
* Loading and emptying : emptying by pumping or gravity pump capacity 600 liters/min at 600 r.p.m
* Attachments :
| a- Hose locker |  |  |  | Two, both sides of tank shell
| b- Ladder |  |  |  | One, at left side in rear of tank
| c- Tool box |  |  |  | One, mounted on frame
| d- Bumper |  |  |  | One ,rear end of chassis frame
| e- Fire extinguish |  |  |  | Two, both side of vehicle
| f- Earth reel |  |  |  | One, at left side of vehicle
| g- Earth chain |  |  |  | One, at rear of vehicle
| h- Muffler with spark arrested |  |  |  | One, provided at front side of vehicle
* Accessories :
| a- Hose (for suction or delivery) 63mm X 3mm | [8 empty] | 2 PCS
| b- Hose wrench | [8 empty] | 2 PCS
* Dip stick is Marked on every 1000 liters
B- Cesspool Emptier Tank
* Cap : 8000 Liters
* Type : Elliptical cross sectioned cylindrical tank
* Tank construction : Tank assembly is elliptical shape, and constructed with steel plate by electric welding it consists of tank sheu, and plates, a main manhole, peep holes, 2-way ball valves and blind manholes. Interior surface of tank is zinc painted for anti- corrosion.
* Loading and emptying : By vacuum pump ( by increasing or decreasing tank pressure).
Pump capacity : 2.790 lit/min at 500 r.p.m
* Equipment :
| a- Delivery hose |  |  |  | 75mm dia x 6m |  |  |  |  | 1 PC
| b- Suction hose |  |  |  | 65 dia x 10m |  |  |  |  | 1 PC
| c- Tool box |  |  |  | one mounted on frame
* Color : Finish coat, crystal white
C – (Drinking Water Tank)
* Capacity : 10.0 KL Drinking water
* Type : Elliptical cross sectioned cylindrical tank
* Tank construction : tank assembly of Elliptical shape, constructed with stainless plate by electric welding which consists of all its part.
And the tank has the parts and equipment that is necessary in the use and carrying the drinking water
* Loading and emptying:
Loading by pumping and by normal feeding from upper manhole
Emptying : by pumping and by gravity
02-06-00705 | over head projection | [8 empty] | 20
02-06-00706 | slide projection | [8 empty] | 20
02-06-00707 | flower making machine | [8 empty] | 20
flower making machine with spaer parts warranty 2 years maintenance two years capacity one ton per hours (1000kG/HR)
02-06-00708 | grain crushing mashine mashine | [8 empty] | 20
grain crushing mashine mashine with four different pore size sleeve capacity one ton per hour (1000KG/HR)
02-06-00709 | mixer | [8 empty] | 20
mixer capacity (1000 KG/HR)
02-06-00710 | oven | [8 empty] | 30
oven with fan- hot air for drying animal food medium size
02-06-00711 | pasute making machine | [8 empty] | 20
pasute making machine capacite 100 KG/HR
02-06-00712 | hot water boiler 2.5 ton /hr | [8 empty] | 20
02-06-00713 | sealed-acid battery 70A/H/long life | [8 empty] | 1200
02-06-00714 | sealed-acid battery 135A/H-long life | [8 empty] | 30000
02-06-00715 | sealed-acid battery 200A/H-long life | [8 empty] | 1000
02-06-00716 | Ni-cd-battery 6A/H 6V | [8 empty] | 400
Targeted Nutrition Programme
02-06-00717 | field vehicle Transportion of supplies and Monitoring / supervision of the programme 200 (2 cars / district + 26 for govermorat and central levels ) | [8 empty] | 400 each
02-06-00718 | Computer (1 per grovermorat , 2 of Baghdad and 4 for NRI) to improve CCCU/PHC database | [8 empty] | 40each
02-06-00719 | Fork lift 3 ton ( to be used storage places at Govermorate for high protein biscut and therapeutic milk) | [8 empty] | 40each
02-06-00720 | Motorcycle (one for each PHC center for monitoring at field level ) | [8 empty] | 2000 each
02-06-00721 | electric cooking heater (for use at PHCs) | [8 empty] | 6,200 each
02-06-00722 | ceiling fans (for use at PHCs/CCCUs) | [8 empty] | 6,200 each
North of Iraq / health
02-06-00723 | Water tank trunk 8-10000 liter capacity , LHD with Export Specs for Iraq & manuf. Recommended spare for 2 yrs. Operation | [8 empty] | 2
02-06-00724 | equipment :Oxygen factory | [8 empty] | 10
1-type (10X-100)
2-production capacity 100 liter/hour
3-purity99.5-99.9%
4-voltage 380V
5-current 600-100A
6-oxygen container of 22000 liter with
a- oxygen gas pump
b-charging desk
02-06-00725 | equipment :sterilizing water for theter room ultraviolet water purifiers | [8 empty] | 20
Water sterilizing system to treat water for theater rooms. The system is to deliver water at a rate of 1 l/s. The system should include any pumping system required to insure adequate operation of the system, where the inlet pressure is between 0.5-1.5 bar. The price should include;
_ installation of the system,
- 2 years full warranty,
_ 3 years maintenance post warranty period,
_ training of professionals at the manufacturer factory (ies), and
_ Local training of staff.
The offer should include a detailed priced list of recommended spare parts for 5 years of operation, along with a schematic diagram of the system showing the location of each part.
An irrecoverable complete sample system should be delivered along with the offer.
The system should be composed of the following units;
A- A pretreatment filtration unit of (2-3) stages with the final stage of pore size less than 1μ.
B- UV sterilization unit with adequate power to insure efficient sterilization of water. The unit should;
_ be of stainless steal,
_ have quick lamp change,
_ have lamp life not less than 8000-10000 hours of continuous operation
_ Have UV intensity sensor and control unit with indicator light.
02-06-00726 | freeze dryes | [8 empty] | 5
malti shell
shell area 5m^2
temp range -50 _ +70
vacum pump 10m^3/hr 220 _ 240V
02-06-00727 | deep freezer | [8 empty] | 10
stainless steel intesior
capacity 200 _ 250 liters
miuoprocessor control
digital display
tempretare -220 _ -85C 220 _ 240V
02-06-00728 | vacum packiging + sealing | [8 empty] | 10
machine 220 - 240V
02-06-00729 | laminas flow cabinet | [8 empty] | 10
with bench _ speed control
rate 100 fpm 220 _ 240V
02-06-00730 | analytical balance | [8 empty] | 10
weishing capasity 205gm 220 _ 240V
02-06-00731 | drying / sterilization cabin | [8 empty] | 10
(bio haz and # biological
UV light 220 _ 240v
02-06-00732 | A W U.(air washer unit) | [8 empty] | 10
tupe 2 bank conter flow type centerfugul single suction fan
fan section :-back ward 2nclined blade
sizedia.:- 750mm
width 188mm
no V-belt :-3
jupply air volume 25900 cmH X 106MMAQ
retunn air volume OCMH,out door air volume 25900 CMH
motor 15KW , 3Q , 380V , 50HZ heatring coil
air section :capacity :- 144000 KCAr/H
watir flow rate 200L/min
water temp (in-out) 83c/71c
air temp:-(in-out) (-1.0-15.0)
rows & fin ptch 2rows x 2.9mm hatinial copper tube aluminin
filter ass.:- NBS 35%
02-06-00733 | . Tyres and Tubes Required For Health Institutions in Iraq
| 600 x 14 | [8 empty] | 1500
| 650 x 14 | [8 empty] | 1500
| 700 x 15 | [8 empty] | 2000
| 750 x 16 | [8 empty] | 1500
| 205 x 16 | [8 empty] | 1500
| 650 x 16 | [8 empty] | 1000
| 1200x 20 | [8 empty] | 1000
| 1100x 20 | [8 empty] | 1000
| 1200x 24 | [8 empty] | 500
| 1000x 20 | [8 empty] | 250
02-06-00734 | computer
| computer network to cover pentium 111 with acc:malti media | [8 empty] | 50
| digital camera | [8 empty] | 10
| P.C viewer | [8 empty] | 10
| scanner | [8 empty] | 38
| colour printer | [8 empty] | 12
| printer-laser jet | [8 empty] | 84
| portable screen | [8 empty] | 38
| C.D read-write | [8 empty] | 10
| C.D row | [8 empty] | 2500
| flophy disc | [8 empty] | 6000
| video blaster with cammera | [8 empty] | 13
| modem | [8 empty] | 40
02-06-00735 | battery charger
| typ |  | capacity |  | power KW | charging current | out put voltage | in put voltage
| cadmium Qsc50-86 |  | 50AH/5HR |  | 2.1KW | 15A | E130-DCV | 380V |  | 10
| QE200E-20 |  | 200AH/HR |  | 1.36KW | 40A | F27-DCV | 380V |  | 10
| QE200E-20 |  | 200AH/HR |  | 1.36KW | 40A | E29.4-DCV | 380V |  | 10
| Qfw600E-20 |  | 600AH/HR |  | 3.4KW | 100A | F27-DCV | 380V |  | 10
| QKC80E-40 |  | 80AH/5HR |  | 1.92KW | 13. 75 | F56.8DCV | 220V |  | 10
| QKC80E-40 |  | 80AH/5HR |  | 1.92KW | 13. 75 | E60.8DCV | 220V |  | 10
02-06-00736 | Mobile lab. For air pollution monitoring (sampling and analysis system)containing ( high volume sampler for measuring total suspended particulates (T.S.P.) , carbon monoxide (CO)analyzer ,Sulfur Oxides (SOx)analyzer ,Total hydrocarbon (THC)analyzer, ozone (o3) analyzer, hydrogen sulfide (H2S analyzer) with standard calibration gases for the above analyzers instuments for measuring the meteorological parameters (wind speed & direction , temp, and humidity) in addition to especially programmed computer and calibration unit and data handling unit for the above instruments and electrical power generator | [8 empty] | 20
02-06-00737 | Mobile water lab. Carried by a car containing ( pH meter , turbidometer, portable spectrophotometer & spectrophotometer with U.V lamp , dissolved oxygen meter, COD reactor , TOC analyzer, deionizer , distillator , refrigerator , electrical generator | [8 empty] | 20
02-06-00738 | Mobile lab. for monitoring Environmental Background Radiation with all accessories containing : | [8 empty] | 15
02-06-00739 | Sodium iodide crystal with multichemical analyzer | [8 empty] | 15
02-06-00740 | Portable dust samplers | [8 empty] | 15
02-06-00741 | Portable dose (dose- rate) meter | [8 empty] | 15
02-06-00742 | automatic developing and fixing system for processing personal films | [8 empty] | 10
02-06-00743 | Accessories for Rotork analysis model 400 - CO analyzer (Rotork co ) :- | [8 empty] | 10
02-06-00744 | Mannual for model 400dual been infrared analyzer | [8 empty] | 10
02-06-00745 | Calibration gas cylinder ( 50 ppm ) | [8 empty] | 10
02-06-00746 | boat for river survay ( 8 horse , using benzene as fule capacity 7 persons | [8 empty] | 32
02-06-00747 | power supply
| V in-pot |  | V out-pot |  | AM | KW | capaste battrey |  |  | QTY
| 24V DC |  | 380V DC |  | 30A | 15KW | 182*2 |  |  | 52
02-06-00748 | Passengers intercity staff bus .40 to 50 passengers,automatic doors ,diesel engine,air condtioned,apholestered chairs stainless steele fram,sliding glass windows with curtains,rubber mat floor, tinted windshield , stereo radio-recorder,ceiling hanging grips, | [8 empty] | 500
AXIAL AEROFOIL AND PROPELLER EXHUST FAN
| fan NO. | block location | TYPE | capacity m3/hr | no. req | external static pressure m.w.a | input kw |  | electric characterishi
02-06-00749 | R.F16 | B | axial aerofoil with motor inside case. | 14000 | 10 | 10 | 4 |  | 380/3/50
02-06-00750 | R.F17 | A | axial aerofoil with motor inside case. | 5950 | 10 | 5 | 2.5 |  | 380/3/50
02-06-00751 | R.F18 | A | axial aerofoil | 4180 | 10 | 7 | 2.5 |  | 380/3/50
02-06-00752 | RF.19 | A | axial aerofoil | 5830 | 10 | 10 | 3 |  | 380/3/50
02-06-00753 | RF.20 | A | axial aerofoil | 2870 | 10 | 10 | 1.5 |  | 380/3/50
02-06-00754 | RF.21 | A | axial aerofoil | 4280 | 10 | 6 | 1.5 |  | 380/3/50
02-06-00755 | RF.22 | A | axial aerofoil | 2500 | 10 | 7 | 1 |  | 380/3/50
02-06-00756 | RF.23 | A | axial aerofoil | 5000 | 10 | 7 | 3 |  | 380/3/50
02-06-00757 | EX.6 | A"-ground | axial wall mounted | 1200 | 10 | 5 | 0.3 |  | 1/220/50
02-06-00758 | EX.7 | A"-ground | axial wall mounted | 2400 | 10 | 5 | 0.6 |  | 1/220/50
02-06-00759 | EX.8 | A"-ground | axial wall mounted | 450 | 10 | 3.5 | 0.2 |  | 1/220/50
02-06-00760 | EX.9 | A"-ground | axial wall mounted | 700 | 10 | 3 | 0.2 |  | 1/220/50
02-06-00761 | EX.10 | A"-ground | axial wall mounted | 3400 | 10 | 6 | 0.6 |  | 1/220/50
02-06-00762 | EX.11 | A"-ground | axial wall mounted | 1900 | 10 | 4 | 0.4 |  | 1/220/50
02-06-00763 | EX.1 | C1 | propellen | 2550 | 10 | 4 | 0.2 |  | 1/220/50
02-06-00764 | EX.2 | C2 | propellen | 1100 | 10 | 0 | 0.1 |  | 1/220/50
02-06-00765 | EX.3 | A" | propellen | 850 | 10 | 3 | 0.1 |  | 1/220/50
02-06-00766 | EX.5 | doct | propellen | 1000 | 10 | 0 | 0.08 |  | 1/220/50
02-06-00767 | EX.4 | general | propellen | 500 | 80 | 0 | 0.07 |  | 1/220/50
ROOF EXTRACTOR SCHEDULE
02-06-00768 | RE-5 | A"-first | roof extrachter | 1600 | 10 | 8 | 0.5 |  | 220/1/50
02-06-00769 | RE-6 | A"-first | roof extrachter | 500 | 10 | 5 | 0.2 |  | 220/1/50
02-06-00770 | RE-25 | A"-ground | roof extrachter | 1800 | 10 | 8 | 0.5 |  | 220/1/50
02-06-00771 | RE-26 | A"-ground | roof extrachter | 700 | 10 | 5 | 0.4 |  | 220/1/50
02-06-00772 | RE-27 | A"-first | roof extrachter | 1300 | 10 | 5 | 0.4 |  | 220/1/50
02-06-00773 | RE-36 | A"-first | roof extrachter | 500 | 10 | 3 | 0.1 |  | 220/1/50
02-06-00774 | RE-17 | B-ground | roof extrachter | 300 | 10 | 5 | 0.2 |  | 220/1/50
02-06-00775 | RE-18 | B-ground | roof extrachter | 1200 | 10 | 15 | 2 |  | 3/380/50
02-06-00776 | RE-19 | B-ground | roof extrachter | 3400 | 10 | 12 | 2 |  | 3/380/50
02-06-00777 | RE-20 | B-ground | roof extrachter | 2210 | 10 | 12 | 2 |  | 3/380/50
02-06-00778 | RE-21 | B-ground | roof extrachter | 1530 | 10 | 10 | 2 |  | 1/220/50
02-06-00779 | RE-22 | B-ground | roof extrachter | 1020 | 10 | 8 | 0.7 |  | 1/220/50
02-06-00780 | RE-23 | A"-ground | roof extrachter | 2430 | 10 | 7 | 0.7 |  | 1/220/50
02-06-00781 | RE-35 | A"-ground | roof extrachter | 1000 | 10 | 6 | 0.7 |  | 1/220/50
02-06-00782 | RE-34 | A"-ground | roof extrachter | 500 | 10 | 5 | 0.5 |  | 1/220/50
02-06-00783 | battery charger
| 24 VDC/ UP TO 100 AMP | [8 empty] | 200
| 12 VDC/20 A | [8 empty] | 100
| 110 VDC/60A | [8 empty] | 40
| (12 - 96 ) VDC/10A | [8 empty] | 10
| variable (12-48)V / UP to 60 A | [8 empty] | 50
02-06-00784 | kerosene refrigertor 13ft | [8 empty] | 10
02-06-00785 | kerosene refrigertor 16ft | [8 empty] | 10
02-06-00786 | telephone exchange system | [8 empty] | 5
capasity :- 50 line
02-06-00787 | water treatment plans | [8 empty] | 3
first :plan componemts
| 1- primary water tank (1m^3) | [8 empty] | 1
| 2- duplex primary water pumps (6m^3/h,2.5bar | [8 empty] | 2
| 3-pirmary filters (25u) | [8 empty] | 6
| 4-duplex water softeners (cataionic,5m^3/h) | [8 empty] | 2
| 5-seconddry filters (5u) | [8 empty] | 6
| 6-duplex revers osmosis units (750L/hr) | [8 empty] | 2
| 7-stainless steel final tanks 1.5m^3 | [8 empty] | 1
| 8-duplex finaly water pumps (6m^3/h , 2.5 bar) | [8 empty] | 2
| 9-distillation water electrical system (750L/hr) | [8 empty] | 1
second:special conditions
1-seller should install , operate and check the plant
2-seller should supply 5 - years spare parts
3- seller should supply operation and maintenance catologes
4- seller should train the technical staff during installation and intiol start-up in site and factory
02-06-00788 | fire water pump
| typ | power | REV sec | suction MM | dishiarge MM |  | capacity L.S | head M
| horizontal | 3 | 1500 | 73.2 | 73.2 |  | 5 L.S | 15m |  | 5
02-06-00789 | water pump for tank
| typ | power | REV sec | suction MM | dishiarge MM |  | capacity L.S | head M
| horizontal | 0.75 | 1500 | 24.4 | 24.4 |  | 1.5 L.S | 15m |  | 5
electrical distribution
| item |  | no. of phases |  | no. of polese |  | voltage | amper
02-06-00790 | circuit breaker |  | 3 |  | 4 |  | 380V | 60A |  | 600
02-06-00791 | contractor |  |  |  | 4 |  | 380v | 60A-40A |  | 400
02-06-00792 | over load |  |  |  | 3 |  | 380v | 60A-40A |  | 400
02-06-00793 | switch | [5 empty] | 380v |  |  | 60
02-06-00794 | oxygen suplply station |  |  | and equipment | [5 empty] | 10
02-06-00795 | flometer oxygen center : adapter | [8 empty] | 40
02-06-00796 | telephone instrument
| telephone instrument:- analogve type using both tone and pulse dialing ,suitable for electronic and cross bar exchanges | [8 empty] | 10000
fan coil unit
| No. of fan | No. of motor |  | type of fan coil unit |  | water temp. (in-out)c |  | capacity (ton) |  | Qty.
02-06-00797 | 2 | 1 |  | chiding horizontal |  | 90 |  | 20 |  | 16
02-06-00798 | 21 | 21 |  | chiding horizontal |  | (6 - 10) , (15 - 20) |  | (1/4) |  | 120
02-06-00799 | 2 | 1 |  | chiding horizontal |  | (8 - 12) |  | (2-3) |  | 84
02-06-00800 | 2 | 1 |  | chiding horizontal |  | (8-6) , (58-60) |  | 550m^3/h |  | 684
02-06-00801 | 2 | 1 |  | chiding horizontal |  | _ |  | 1 |  | 400
02-06-00802 | motor control board
complete motor control board , 3ph , star - delta starting with all nessecery contacters and fuses and protection devises , the power of the motor as bellow
| 3.5KW | [8 empty] | 50
| 4.5KW | [8 empty] | 50
| 5.5KW | [8 empty] | 50
| 15KW | [8 empty] | 50
| 11.5KW | [8 empty] | 50
| 55KW | [8 empty] | 50
| 75KW | [8 empty] | 50
| 22KW | [8 empty] | 100
| 30KW | [8 empty] | 50
02-06-00803 | briller type writer | [8 empty] | 200
german type (portable)
02-06-00804 | record cassette japanese from (60) minate | [8 empty] | 1000
02-06-00805 | record cassette (with out radio) japanese origin or european origin | [8 empty] | 200
02-06-00806 | full set of kits for repairingmaintainins equpment (microelectronic equpment) hearing aids | [8 empty] | 20
02-06-00807 | computer screen for weak resion person (weak sighted ) | [8 empty] | 10
02-06-00808 | duplicator recorder cassette | [8 empty] | 10
02-06-00809 | electrical fitting
| required matrial |  |  | power |  | voltage |  | size |  | qty.
| fluoresent |  |  | 35W |  | 220V |  | TLD 4x35 |  | 1000
02-06-00810 | chilled water pump
| kw | r.p.m | Q L/S | Hm | QTY
| 4 | 1500 | 41 | 7.5 | 40
| 5.5 | 1500 | 20 | 20 | 100
| 11 | 1500 | 27 | 35 | 60
| 15 | 1500 | 30 | 30 | 60
| 22 | 1500 | 65 | 24 | 40
| 30 | 1500 | 42 | 42 | 200
| 20 | 3000 | 45 | 24 | 5
02-06-00811 | water pump forsenitary (hot water)
| kw | r.p.m | Q L/S | Hm | QTY
| 3 | 3000 | 8.3 | 32 | 50
| 5.5 | 1500 | 7 | 35 | 50
| 11 | 3000 | 5.5 | 50 | 20
02-06-00812 | water pump for tank
| kw | r.p.m | Q L/S | Hm | QTY
| 0.75 | 3000 | 1.5 | 60 | 500
| 3 | 1500 | 5 | 30 | 200
| 5.5 | 1500 | 10 | 30 | 100
| 7.5 | 1500 | 40 | 20 | 20
| 15 | 1500 | 16.6 | 44 | 50
| 22 | 1450 | 28 | 40 | 20
| 7.5 | 3000 | 1.25 | 85 | 25
02-06-00813 | 1) Galvanized Steel Pipes And Fittings
Galvanized steel pipes and fitting conforming to BS 1387 or equivalent with 10 bar working pressure, all joints shall be screwed to B.S. 21 up to 50mm diameters, on large diameters (65mm and over) flanged joints shall be used.
Flange shall be conforming to B.S 4504 part 1.
| 1-1) Piping:- O 15 mm (6m length /piece) | [8 empty] | Pieces | 2500
| O 20 mm | [8 empty] | = | 2000
| O 25 mm | [8 empty] | = | 1500
| O 32 mm | [8 empty] | = | 1000
| O 40 mm | [8 empty] | = | 1000
| O 50 mm | [8 empty] | = | 1500
| O 65 mm | [8 empty] | = | 1000
| O 75 mm | [8 empty] | = | 1000
| O 100 mm | [8 empty] | = | 500
1-2) Ditto:- but with 15 bar working pressure
| O 100 mm (6m length / piece) | [8 empty] | Pieces | 500
| O 150 mm | [8 empty] | = | 300
02-06-00814 | 2) Copper Pipes And Fittings
2-1) Copper tubes and compression or capillary fittings to BS 2871 part 1 table x
| O 10 mm | [8 empty] | M.L | 5000
| O 15 mm | [8 empty] | = | 7500
| O 22 mm | [8 empty] | = | 7500
| O 28 mm | [8 empty] | = | 7500
| O 35 mm | [8 empty] | = | 5000
| O 42 mm | [8 empty] | = | 5000
| O 54 mm | [8 empty] | = | 5000
| O 67 mm | [8 empty] | = | 5000
| O 76.1 mm | [8 empty] | = | 6000
| O 108 mm | [8 empty] | = | 4000
| O 159 mm | [8 empty] | = | 3500
2-2) Ditto:- but to BS 2871 part 1 table T with fittings
| O 35 mm | [8 empty] | M.L | 3000
| O 42 mm | [8 empty] | = | 3000
| O 54 mm | [8 empty] | = | 5000
| O 67 mm | [8 empty] | = | 4000
| O 76.1 mm | [8 empty] | = | 4000
| O 108 mm | [8 empty] | = | 3500
02-06-00815 | 3) Ductile Iron Pipe And Fittings
Ductile iron pipes and fittings according to BS 4772 jointing should be flanged type with rubber gasket with 15 bar working pressure.
| O 75 mm (6 m length / piece) | [8 empty] | Pieces | 500
| O 100 mm | [8 empty] | = | 750
| O 125 mm | [8 empty] | = | 750
| O 150 mm | [8 empty] | = | 1000
| O 200 mm | [8 empty] | = | 2000
| O 250 mm | [8 empty] | = | 1500
| O 300 mm | [8 empty] | = | 1500
| O 350 mm | [8 empty] | = | 1500
| O 400 mm | [8 empty] | = | 1000
02-06-00816 | 4) Cast Iron Pipes And Fittings
4-1) Socketless cast iron pipes and fittings in
accordance with BS 437 or equivalent for drain pipes and fittings complete with coupling and rubber gasket
| O 50 mm (3m length / piece) | [8 empty] | Pieces | 1000
| O 75 mm | [8 empty] | = | 500
| O 100 mm | [8 empty] | = | 1250
| O 150 mm | [8 empty] | = | 1000
| O 200 mm | [8 empty] | = | 1000
| O 250 mm | [8 empty] | = | 1200
| O 300 mm | [8 empty] | = | 750
4-2) Ditto, but conform to BS 416 for soil, waste and ventilation
| O 50 mm (3m length / piece) | [8 empty] | Pieces | 750
| O 75 mm | [8 empty] | = | 500
| O 100 mm | [8 empty] | = | 1000
| O 150 mm | [8 empty] | = | 500
| O 200 mm | [8 empty] | = | 350
4-3) Ditto, but conform to BS 460 for roof drainage
| O 75 mm (3m length / piece) | [8 empty] | Pieces | 250
| O 100 mm | [8 empty] | = | 750
| O 150 mm | [8 empty] | = | 300
4-4) Ditto, but for roof outlets
- vertical type
| O 75 mm | [8 empty] | NOS | 50
| O 100 mm | [8 empty] | = | 100
| O 150 mm | [8 empty] | = | 70
- horizontal type
| O 75 mm | [8 empty] | NOS | 50
| O 100 mm | [8 empty] | = | 100
| O 150 mm | [8 empty] | = | 60
02-06-00817 | 5) Sectional Pressed Steel Tanks
Sectional pressed steel tanks shall be consists of (1x1)m dimensions galvanized plates modular or (1.22 x 1.22) m to BS 1564. All plates shall be of 6 mm thickness, the cover shall be of 3 mm thickness. The tanks have compartments. The tank plate shall be of external flange construction and bolting with suitable gasket materials. All piping connections shall be flanged type.
The tank should be provided with all necessary accessories such as floats ventilators, manhole opening, inside and outside ladder, over flow and drain pipes with level indicator …. Etc.
Strip jointing must be provided for all joints.
| 5-1) Pressed steel tank of 100 m³ | [8 empty] | No. | 1
| 5-2) Pressed steel tank of 280 m³ | [8 empty] | No. | 1
02-06-00818 | 6) Water Service Booster Pump Set
6-1) Three centrifugal pumps, direct coupled,
end suction type arranged to run as two duty/one
standby. The pumps have the following
specifications:
Q= 15m³/hr - H= 65m
Casing:- cast iron
Impeller:- bronze
shaft:- stainless steel
Seal:- mechanical
Insulation:- class F
IP:- 54 suitable for 380V/ 3pH/ 50Hz
6-2) Two pneumatic pressure vessel of 2m³ capacity and 10 bar working pressure.
complete with oil free compressor
6-3) All necessary accessories such as isolating
valves on suction and discharge, non return valves, pressure and flow gauges, pressure swtiches….etc.
6-4) Control panel
| The whole assembly shall be mounted on a purpose mode base from complete with steel pipe work, pipe supports and lifting lugs. | [8 empty] | unit | 1
02-06-00819 | 7) Fire Fighting Pumps Set (Wetriser)
7-1) Ditto, as item 6-1, but two multistage pumps (horizontal type, one duty / one stand by)
Q= 90 m³/hr
H= 90M
7-2) Ditto, as item 6-1, but one pump multistage vertical type with Q= 10m³/hr
H= 90M (as Jocky pump)
7-3) Ditto, as item 6-3
| 7-4) Ditto as item 6-4 | [8 empty] | unit | 1
02-06-00820 | 8) Fire Fighting Pumps Set (Hose Reel)
| Ditto, as item (7), but without providing Jocky pump. Q= 8m³/hr - H=75m | [8 empty] | unit | 1
02-06-00821 | 9) Drainage Submersible Pumps Set
Fully automatic drainage pump set, comprises of two pumps, non clogging type, motor squirrelcage, 3pH with class F insulation, complete with guide rails for retaining pump position, and chain shall be attached to the pump. The set shall be complete with isolating valves, non return valves, pressure swtiches...etc. Electrical floats shall be provided to control water level.
Casing:- cast iron
Impeller:- cast iron
shaft:- stainless steel
Seal:- mechanical
| 9-1) Q= 25m³/hr - H=10M | [8 empty] | unit | 10
| 9-2) Q= 20m³/hr - H=12M | [8 empty] | unit | 10
| 9-3) Q= 15m³/hr - H=12M | [8 empty] | unit | 10
| 9-4) Q= 10m³/hr - H= 10M | [8 empty] | unit | 10
| 9-5) Q= 5m³/hr - H=12M | [8 empty] | unit | 10
02-06-00822 | 10) Sewage Submersible Pumps
Ditto for sewage submersible pumps:
| 10-1) 20m³/hr - H=10M | [8 empty] | unit | 10
| 10-2) 10m³/hr - H=10M | [8 empty] | unit | 10
| 10-3) 5m³/hr - H=12M | [8 empty] | unit | 10
| 10-4) 3m³/hr - H=12M | [8 empty] | unit | 10
02-06-00823 | 11) Circulating Pumps Units
Electrical inline circulator pumps with vairable velocities. Motor of non-over loading characteristics with by passarrangement, valves, timer… etc. The unit shall be complete with control panel.
| Q= 5m³/hr - H=12 | [8 empty] | unit | 8
02-06-00824 | 12) Make-up Boosting Pumps Set (Cooling Tower)
Ditto as item 6 but with the following specification:-
Q= 20m³/hr
H= 35M
| Complete with two diaphram pressure vessel of capacity 500 liter per each. | [8 empty] | unit | 1
02-06-00825 | 13) Water Softener
Fully automatic douplex softener complete with necessary accessories such as piping, valves, flow meters, pressure gauges complete with control panel … etc.
Flow rate= 20m³/hr
Inlet pressure= 1.5bar
| working pressure= 10bar | [8 empty] | unit | 1
02-06-00826 | 14) Heavy Duty Filters
Fully automatic packaged unit high rate muliti-layered sand filters complete with main operating valves , pipes and fitting ,flow control , controls, filter media and accessories such as pressure gauges ,cocks for inlet and outlet with 10 bar working pressure.
| 14-1) Flow rate 30 m3/hr | [8 empty] | No. | 1
| 14-2) Flow rate 60 m3/hr | [8 empty] | No. | 1
02-06-00827 | 15) Actived carbon Filters
Ditto , but with activated carbon beds with 10 bar working pressure
| 15-1) Flow rate 25 m3/hr | [8 empty] | No. | 1
| 15-2) Flow rate 50 m3/hr | [8 empty] | No. | 1
02-06-00828 | 16) Cast iron adaptor
16-1) Cast iron ( mentioned in item 4 ) adaptor to be connected with upvc pipes conform to BS 4514 . For soil and ventilating pipe :
| 50 mm | [8 empty] | Nos | 100
| 75 mm | [8 empty] | Nos | 80
| 100 mm | [8 empty] | Nos | 100
| 150 mm | [8 empty] | Nos | 60
| 200 mm | [8 empty] | Nos | 45
16-2) Ditto but be connected with pvc pipes
| 50 mm | [8 empty] | Nos | 150
| 75 mm | [8 empty] | Nos | 75
| 100 mm | [8 empty] | Nos | 90
| 150 mm | [8 empty] | Nos | 50
02-06-00829 | 17) Flexible Hose
17-1) Rubber flexible hose used for connection between sanitary fixture and feeding water pipes :-
| working pressure 3.5 bar diam 15 mm | [8 empty] | Nos. | 300
| 17-2) Ditto, but copper hose working pressure 7 bar diam 15 mm | [8 empty] | Nos. | 500
02-06-00830 | 18) Sanitary Fixtures
Vitrus china (or equivelant) sanitary fixtures of white colour .All fixtures shall be of the best quality .
| 18-1) Eastern style we ( 100 mm s trap) supplied with vitrus china cistern of 14 lit capacity complete with ball valve and float .All wcs shall be provided with accessories. | [8 empty] | Nos | 80
| 18-2) Ditto , but "P" trap | [8 empty] | Nos | 75
| 18-3) Ditto , but westeren style wc supplied with cast iron cistern of 14 lit-capacity complete with ball valve and flood, chain.All wc's shall be provided with 32 mm flush pipe and 15 mm chromium flexible hose of 0.75m length and 3.5 bar resisting pressure.The hose completed with 10 mm chromium nozzle. | [8 empty] | Nos | 70
18-4) Ditto ,but wash basin complete with vitrus china stands, shelfs and soap trys.All the wash basins shall be provided with:-
25mm chromium bottle (or"p") trap
| 15mm chromium plated mixer and 3.5 bar resisting pressure | [8 empty] | Nos. | 300
18-5) Ditto ,but bedit complete with:-
- 40 mm chromium plated bottle trap ( or ‘P’)
| -15 mm chromium mixer and 3.5 bar resisting pressure. | [8 empty] | Nos. | 100
18-6) Cast iron shower tray , complete with 15 mm chromium plated mixer with 15 mm flexible chrom. Hose ended with chrom. head shower ( resisting pressure 3.5 bar ) .The flexible hose has the alternative of being fixed on wall.Complete with all accessories such as soap tray …etc
| - Tray size 800x800 | [8 empty] | Nos | 100
18-7) Ditto, but bath tub , complete with
| 15 mm chromium mixer with 15 chromium tube with head shower .The bath shall be provided with MM 15 chromium flexible hose ended with shower . All the bath tubs shall be provided with accessories such as soap tray , chromium handle , 40 mm chromium bottle ‘p’ trap | [8 empty] | Nos | 50
18-8) Ditto as 18-5, but for urinal complete with
- 9 lit vitrus china automatic cisteren complete with flushing pipe
- 32 mm chromium plated bottle trap (‘p’ trap )
| - partitions | [8 empty] | Nos | 60
02-06-00831 | 19) Grease+B778+B753 Trap+B742+B726
| Cast iron grease trap with 100 MM mm outlet with access at ground level, supplied with single seal cover and frame and screwed flange for 50 mm vent , supplied with galvanized sediment pans . | [8 empty] | Nos | 30
02-06-00832 | 20) Covers and Frames
20-1) Medium duty double sealed cast iron cover and frames with the following size :
| REF! C25525 mm | [8 empty] | Nos. | 120
| - 600 x 450 mm | [8 empty] | Nos. | 50
| - 900 x 600 mm | [8 empty] | Nos. | 70
20-2) Ditto, but heavy duty
| - Diam 550 mm | [8 empty] | Nos. | 200
20-3) Ditto, but heavy medium grating and frames
| 600 x 450 | [8 empty] | Nos. | 100
20-4) Ditto, but for Hydrant cover and frame
| 500 x 350 | [8 empty] | Nos. | 100
20-5) Ditto, but special purpose covers and frames have a single seal and supplied with 4 brass screws.
| The top is recessed for filling to material match the surrounding surfaces. | [8 empty] | Nos. | 75
20-6) Ditto, but roadway gratings and frames
| 500 x 350 | [8 empty] | Nos. | 500
20-7) Ditto, but heavy duty cast iron channel grating , supplied with lugs cast at 30 cm centers.
| Size 100 x 30 cm | [8 empty] | Nos. | 500
02-06-00833 | 21) Pillar Fire Hydrant
| 21-1) A piller fire hydrant consists of a body equipped with "3" nozzles , one forward 100 mm and two side ways 65 mm . The body projects a bove ground level .The valve box containing the closure device below ground between these two main 100 mm diam. stand pipe , the hydrant shall be completed with a screw - down system for opening and closing , automatic drainage device and on air inlet device . All the iron fire hydrant are coated with red polyurethane paint , the threading shall be to BS 750 | [8 empty] | Nos. | 50
| 21-2) Ditto,but consists of 2 nozzels 80 mm forward nozzel and 65 mm side way nozzel | [8 empty] | Nos. | 50
21-3) Ditto , but fire and washing hydrant consists of iron body . The box enclosing on outlet nozzel . It has a detachable ductile iron lid.
| 80 mm hydrant | [8 empty] | Nos | 50
65mm nozzel
02-06-00834 | 22) Hose Real & Wet Riser / Cabinet
22-1) Hose real cabinet accomodates a manually or automatically operated swinging hose reel which can be combined with a matching wer riser or extinguisher cabinet .
Door have right opening and swing through a full 180 :
Size :- 1350 x 810 x 355 mm
Construction :- steel . Door panel shall be provided with stainless steel finger panel
Capacity :- 30 x 19 mm dia
Nozzle :- jet ( hose reel )
| Pressure:- max. operation pressure 10 bar | [8 empty] | Nos. | 25
22-2) Ditto, swinging open wall hose reel
Diam:- 560 mm
Overall height:- 610 mm
| Width:- 250 mm | [8 empty] | Nos. | 10
02-06-00835 | 23) Dimener lized water
Full automatic , Duplex Dimenerlizer complete
with necessary accessories such as piping ,
regulating valves ,valves , flow meters , pressure
gauges complete with control panel ….etc.
- flow meter 25 m3/hr
- inlet pressure 1.5 bar
| - working presure 10 bar | [8 empty] | set | 1
02-06-00836 | 24) Distilled Water
Ditto , but Duplex Distiller , but of flow rate
| 20 m3/hr | [8 empty] | set | 1
02-06-00837 | Centrifugal Water Chiller
Type - Centrifugal , water cooled
Compressor and motor
The compressor - motor combination shall be Hermatic
construction complete with starter and capacitor for
power factor correction .The motor power is 3-phase
380 volt, 50 HZ with main power factor of o.91 at full
load
Cooler and Condenser
Cooler and condenser shall be shell and tube designed for
( 10 ) atm water side working pressure
Control Panel
Automatic control panel shall be electronic type including
all safety devices.
Evaporator Data
Fouling factor =0.0002
m2.hr.Cْ/Kcal
Ent. Water temp .=11.6Cْ
Leav. Water temp .=6 Cْ
Max. water pressure drop =6 M.water Gauge
Condenser Data
Fouling factor= 0.0004
m3.hr.Cْ/kcal
Ent. Water Temp = 29.4 Cْ
Leav. Water Temp =35 Cْ
Max. water pressure drop =7 M.water Gauge
Capacity
| 1200 000 kcal/hr | [8 empty] | 4 | Nos.
( 400 ton )
02-06-00838 | Hot Water Boiler
Type IN _ LINE
Electric
Tank
shall be constructed from low carbon steel - working
pressure 7.5 bar
Heating
Elements shall be of immersion type copper sheath of
11.6 watt/cm2 max.density
Control
proportional temperature control with multi - step control
complete with control board and all safety devices
| capacity 650 kw | [8 empty] | Nos | 4
02-06-00839 | Pumps
Type
End - section centrifugal oase mounted , direct coupled
Impeller Material
Bronze
Shaft material
stainless steel
seal -Mechanical
Motor
squirrel cage, drip proof type 1450 R.P.M
Base Material
cast iron or welded steel
chiled water pump capacity 61 L/S
| Head 45 m | [8 empty] | Nos. | 4
Hot water pump capacity 14 L/S
| Head 42 m | [8 empty] | Nos. | 4
Condenser water pump
capacity 76 - L/S
| Head 18 m | [8 empty] | Nos. | 4
02-06-00840 | Cooling Tower
Type- outdoor
forced draft
casino - hot dip
galvanized steel of min thickness 1.6 mm
Lowers , eliminators
and air inlet screen are hot dip galvanized steel
Full: shall be polyvinal
Basin-
shall be hot dip galvanized steel of min - thickness 3.5 mm
Water distribution
shall be galvanized steel pipes with bronze non - clog
spray nozzles
Motors
Outdoor use with class " F" insulation
Electric power
3 phase / 380v/50HZ
Water Temp
IN- 35 Cْ
out 29.4 Cْ
Out door wet bulb
temp- 27 Cْ
Heat Rejection Capacity
| 1500 000 K cal/ HR | [8 empty] | Nos | 4
02-06-00841 | Roof Top Packaged
A/C unit - Air Cooled
Max ambient outdoor working temp -52Cْ
Entering Air temp to condenser -46Cْ
Unit shall be complete with filter thermostat
| Capacity 69000 kcal/hr | [8 empty] | Nos. | 10
| Capacity 56000 kcal/hr | [8 empty] | Nos. | 8
| Capacity 45000 kcal / hr | [8 empty] | Nos. | 8
| Capacity 33000Kcal / hr | [8 empty] | Nos. | 6
02-06-00842 | Roof Ventilator
Horizantal dischange
Power 400v/3ph/50 hz
Unit shall be complete with back draught
shutter, bird guard
local isolating switch
and speed control
External static
pressure 6mm .W.G
| Capacity 1200 m3/hr | [8 empty] | Nos. | 10
| Capacity 2000 m3/hr | [8 empty] | Nos. | 10
| Capacity 3000 m3 /hr | [8 empty] | Nos. | 10
| Capacity 4000 m3/hr | [8 empty] | Nos. | 10
02-06-00843 | Supply Air Linear slot diffuser
Diffuser shall be constructed from Aluminum natural colour
solt width 19mm
integral volume control damper,fully adjustable from the face of the diffuser
complete with air deflection blode+B400s,mounting bracket.
| A) 3 SLOT | [8 empty] | M.L | 1000
| B) 4 SLOT | [8 empty] | M.L | 1000
| C) 5 SLOT | [8 empty] | M.L | 600
02-06-00844 | Supply Air square diffuser
alumin. construction
complete with volume control damper of opposed blade type
| A) size (neck)mm 225x225 | [8 empty] | Nos. | 200
| B) 300x 300 | [8 empty] | Nos. | 300
| C)375 x 375 | [8 empty] | Nos. | 300
02-06-00845 | Supply Air Re+B224gister
aluminum construction with volume control damper.
adjustable front horizantal bars and rear vertical adjus. bars
neck size ( B x H) mm
| 400 x 150 | [8 empty] | Nos. | 100
| 500 x 150 | [8 empty] | Nos. | 100
| 600 x 150 | [8 empty] | Nos. | 100
| 700 x 150 | [8 empty] | Nos. | 100
| 800 x 200 | [8 empty] | Nos. | 100
| 900 x 200 | [8 empty] | Nos. | 100
02-06-00846 | Exhaust Air Valve
shall be aluminum white colour
complete with counter frame nominal diameter mm
| Diam. 100 | [8 empty] | Nos. | 20
| Diam. 150 | [8 empty] | Nos. | 20
02-06-00847 | Piping
Black steel class B,schedule 40,with 10.5 Kg/cm2, seamless with fittings.B432
pipe size(mm diam.)
| 300 | [8 empty] | M.L | 500
| 250 | [8 empty] | M.L | 1000
| 200 | [8 empty] | M.L | 1000
| 150 | [8 empty] | M.L | 2000
| 125 | [8 empty] | M.L | 2000
| 100 | [8 empty] | M.L | 3000
| 80 | [8 empty] | M.L | 3000
| 65 | [8 empty] | M.L | 3000
| 50 | [8 empty] | M.L | 5000
| 40 | [8 empty] | M.L | 5000
| 32 | [8 empty] | M.L | 5000
| 25 | [8 empty] | M.L | 5000
| 20 | [8 empty] | M.L | 5000
| 15 | [8 empty] | M.L | 5000
02-06-00848 | VALES
cast iron gate valve with flanges 10.5 kg/cm2
| 250 mm | [8 empty] | Nos. | 50
| 200 mm | [8 empty] | Nos. | 60
| 150 mm | [8 empty] | Nos | 60
| 125 mm | [8 empty] | Nos | 60
| 100 mm | [8 empty] | Nos | 60
| 80 mm | [8 empty] | Nos | 40
| 65mm | [8 empty] | Nos | 40
Bronze gate valve serewed end- non-rising stem
| 50 mm | [8 empty] | Nos | 100
| 40mm | [8 empty] | Nos | 100
| 32 mm | [8 empty] | Nos | 100
| 25mm | [8 empty] | Nos. | 100
| 20 mm | [8 empty] | Nos. | 100
| 15 mm | [8 empty] | Nos. | 200
02-06-00849 | Galvanized sheet steel
Galvanized sheet steel (duct moterial)
U.S steel gouge
| 18 | [8 empty] | TON | 25
| 20 | [8 empty] | TON | 50
| 22 | [8 empty] | TON | 50
| 24 | [8 empty] | TON | 25
02-06-00850 | Duct thermal insulation
| fiber glass.flexible blanket type.25mm thick with vapour barrier consisting of 0.05mm aluminium : foil reinforced with kraft paper and glass fibre .Density of 24 kg per cubic meter | [8 empty] | M² | 100 000
02-06-00851 | Pipe insulation
sectional fibre glass with aluminum density of 48 kg/m3, factor applied vapour barrier jacket of minimum 0.05 aluminium foil laminated to kraft paper reinforced with glass fibers.
insulation nominal thickness
Bore(mm) mm
up to 65 25
80-150 40
200 and larger 50
size (mm diam.)
| 300 | [8 empty] | M.L | 500
| 250 | [8 empty] | M.L | 1000
| 200 | [8 empty] | M.L | 2000
| 150 | [8 empty] | M.L | 2000
| 125 | [8 empty] | M.L | 3000
| 100 | [8 empty] | M.L | 3000
| 80 | [8 empty] | M.L | 3000
| 65 | [8 empty] | M.L | 5000
| 50 | [8 empty] | M.L | 5000
| 40 | [8 empty] | M.L | 5000
| 32 | [8 empty] | M.L | 5000
| 25 | [8 empty] | M.L | 5000
| 20 | [8 empty] | M.L | 5000
| 15 | [8 empty] | M.L | 5000
CABLES & WIRES
02-06-00852 | A) Power cables: -
Low tension cables stranded copper
conductors, PVC insulated, all cores color
colour coded PVC inner sheath, high 600/1000 V
impactPVC outer sheath black, rated voltage
voltage 600/1000vgenerally to BS 6346
or to VDE 0271 NYY-J 0.9.86.
| A-1) 4 x 2.5 mm² NYY-J | [8 empty] | M.L | 5000
| A-2) 4 x 4 mm² NYY-J | [8 empty] | M.L | 5000
| A-3) 4 x 6 mm² NYY-J | [8 empty] | M.L | 5000
| A-4) 4 x 10 mm² NYY-J | [8 empty] | M.L | 5000
| A-5) 4 x 16 mm² NYY-J | [8 empty] | M.L | 5000
| A-6) 3 x 25 + 16 mm² NYY-J | [8 empty] | M.L | 5000
| A-7) 3 x 35 + 16 mm² NYY-J | [8 empty] | M.L | 6000
| A-8) 3 x 50 + 25 mm² NYY-J | [8 empty] | M.L | 5000
| A-9 3 x 95 + 50 mm² NYY-J | [8 empty] | M.L | 5000
| A-10) 3 x 120 + 70 mm² NYY-J | [8 empty] | M.L | 5000
| A-11 3 x 150 + 70 mm² NYY-J | [8 empty] | M.L | 5000
| A-12) 3 x 240 + 120 mm² NYY-J | [8 empty] | M.L | 3000
| A-13 3 x 300 + 150 mm² NYY-J | [8 empty] | M.L | 3000
| A-14) 4 x 6 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-15 4 x 10 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-16) 4 x 16 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-17) 3 x 25 + 16 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-18) 3 x 35 +16 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-19) 3 x 50 + 25 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-20 3 x 70 + 35 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-21) 3 x 70 + 35 mm² NYY-J | [8 empty] | M.L | 5000
02-06-00853 | B) Wires:
Single wires, copper stranded core PVC
insulated, rated 70 permanent and160c
short circuit,rated voltage 450/750v
generlally to BS 6004 or to vde 0250
type nya
Packing: 100 yds each coil in specified.
colours
B-1 2.5 mm²
| Red | [8 empty] | Coils | 1500
| Black | [8 empty] | Coils | 1500
| Blue | [8 empty] | Coils | 1500
| Yellow | [8 empty] | Coils | 1500
| Grn/Ylw | [8 empty] | Coils | 1500
B-2 1.5 mm²
| Red | [8 empty] | Coils | 1000
| Black | [8 empty] | Coils | 1000
| Blue | [8 empty] | Coils | 1000
| Yellow | [8 empty] | Coils | 1000
| Grn/Ylw | [8 empty] | Coils | 1000
B-3 4mm²
| Red | [8 empty] | Coils | 500
| Black | [8 empty] | Coils | 500
| Blue | [8 empty] | Coils | 500
| Yellow | [8 empty] | Coils | 500
| Grn/Ylw | [8 empty] | Coils | 500
B-4 6mm²
| Red | [8 empty] | Coils | 500
| Black | [8 empty] | Coils | 500
| Blue | [8 empty] | Coils | 500
| Yellow | [8 empty] | Coils | 500
| Grn/Ylw | [8 empty] | Coils | 500
02-06-00854 | Telephone Cables & Accessories
A) Telephone cables: -
PVC/Bare copper conductor 0.6mm/tinned /PVC
| A-1) 10 pair. | [8 empty] | M.L | 5000
| A-2) 20 pair. | [8 empty] | M.L | 5000
| A-3) 30 pair. | [8 empty] | M.L | 5000
Packing: on wooden drums.
B) Accessories: -
Terminal Box-Flush Mounted
Steel Grey / rust proof + Terminal block.
| B-1) 10 pair. | [8 empty] | No. | 50
| B-2) 20 pair. | [8 empty] | No. | 50
| B-3) 30 pair. | [8 empty] | No. | 50
| B-4) 100 pair. | [8 empty] | No. | 20
02-06-00855 | Conduit & Accessories
A) Size 20mm: -
A-1 Hot dip galvanized heavy gauge steel conduit, screwed both ends, one coupler, 3.75m long to BS 4568.
| coupler, 3.75m long to BS 4568. | [8 empty] | Cond | 10000
A-2 Galvanized circular malleable iron
junction boxes.
| Terminal | [8 empty] | No. | 2000
| Through | [8 empty] | No. | 5000
| Angle | [8 empty] | No. | 2000
| Tee | [8 empty] | No. | 2000
| Intersection | [8 empty] | No. | 3000
B) Size 25mm: -
| B-1 Hot dip galvanized heavy gauge steel | [8 empty] | Cond | 5000
conduit, screwed both ends, one coupler,
3.75m long to BS 4568.
B-2 Galvanized circular malleable iron
junction boxes.
| Terminal | [8 empty] | No. | 1000
| Through | [8 empty] | No. | 1000
| Angle | [8 empty] | No. | 1000
| Tee | [8 empty] | No. | 1000
| Intersection | [8 empty] | No. | 1000
C) Draw in steel tape: -
| C-1 20m length | [8 empty] | No. | 50
| C-2 30m length | [8 empty] | No. | 50
D) Complete set comprising stock
dies & guides: -
| D-1 20+25 mm | [8 empty] | set | 20
02-06-00856 | A -Panel distribution boards:
Three-phase and neutral distribution
borads voltage 415v AC 50 HZ BS 5486
IP230 with door and lock
to fixed in the wall (flush type) with
Earthling terminal bus bars and with
| A-1 Distribution board 6 triple pole MCB | [8 empty] | NOS. | 25
ways
Main in coming 100A MCB three phase
Single poles MCB 15A.10 .NOS
Single poles MCB 30A 8Nos.
| A-2 Distribution board 8 triple pole MCB | [8 empty] | NOS. | 25
ways-
Main in coming 100A MCB three phase
Single poles MCB 15A 15 NOS.
Single poles MCB 30A 9NOS.
| A-3 distribution bord 12 triple pole mcb | [8 empty] | NOS | 25
warpmain Incoming 160 mcb three phase
single pole mcb 15 A 20 Nos
single pole mcb 30 A 16 Nos
A-4 SPARES
| single pole mcb 15 A | [8 empty] | NOS | 100
| single pole mcb 30 A | [8 empty] | NOS | 100
02-06-00857 | Switches and Sockets
A- SWITCHES
Switches 250v 15 or 20 amp
fluch mounting-white cover
| A-1 one way 1 gang | [8 empty] | NOS | 500
| A-2 two way 1 gang | [8 empty] | NOS | 500
| A-3 one way 2 gang | [8 empty] | NOS | 500
| A-4 one way 2 gang | [8 empty] | NOS | 500
| A-5 one way 3 gang | [8 empty] | NOS | 500
| A-6 one way 4 gang | [8 empty] | NOS | 500
B-SWITCHES SOCKETS
3 pin Rectangular bs 2814- 13 or 15 Amp
Fluch mounting-white cover Bs 1863
| B-1 3pin rectangulaectan-13 Amp | [8 empty] | NOS | 5000
| B-2 3pin rectangulaectan-Duplex13 Amp | [8 empty] | NOS | 5000
| B-3 3pin rectangulaectan-15 Amp | [8 empty] | NOS | 5000
| B-4 2Amp Telephone socket | [8 empty] | NOS | 5000
| B-5 T.Vsocket single out let | [8 empty] | NOS | 1000
02-06-00858 | Fire Alarm System
A-1) central Indication and control panel
suitable for 6 fire zones with fire alarm
bell complete with all safety device and
outomatic charger including nickel
cadmium battery with connection to the
| central Indicationg and control board | [8 empty] | No.C741 | 1
A-2)Manual call station break glass units-
surface mounted- red coulour the glasses
| can be supplied in english language | [8 empty] | NOS | 15
A-3) complete with amounting base outomatic
smoke detector off white coulor withvisual
of an alarm is given by red light diode
clearlyn visble on the detector casing
| ambient temp range (0c- 50c) | [8 empty] | NOS | 70
A-4)complete with a amounting base amount-
ing heat detector with visual Indication
of an alarm is given by red- light diode,
clearly visble on detector with base off
| white colour ambient range (0c- 40c) | [8 empty] | NOS | 10
A-5) Indoor fire alarm bell 24v.Ds black poly-
carbonete base.6" hight reliability, long
running life and easy installation,nomain-
| tenace in normal use. | [8 empty] | NOS | 15
02-06-00859 | Light fittings: -
NOTE:
Below mentioned fluorescent fittings .
are security quick startPower factor not
lessthan 0.9 Lagging 240 volt-AC 50HZ.
A-1) 2 x 40w fluorescent fitting with Lamella
| louver -recessed mouting | [8 empty] | NOS | 400
A-2) 2 x 40w fluorescent fitting with Lamella .
| louvre-Surface mounting | [8 empty] | NOS | 250
A-3) 1 x 40w fluorescent fitting with Lamella
| lovre-Recessed mounting. | [8 empty] | NOS | 400
A-4) 1 x 40w fluorescent fitting with Opal
| Diffuser-Surface mounting. | [8 empty] | NOS | 250
A-5) 2 x 20w fluorescent light fitting with
| Opal Diffuser-Surface mounting. | [8 empty] | NOS | 500
A-6)4 x 20w fluorescent light fitting with
| Opal Diffuser-Surface mounting. | [8 empty] | NOS | 500
| A-7)60 X 60 cm Fluorescent light with lamela diffuser | [8 empty] | NOS | 400
02-06-00860 | Aluminum false ceiling closed type with all fixing accessories
| 30 x 60 cms | [8 empty] | M² | 4000
| 30 x120 cms | [8 empty] | M² | 4000
| 60 x 60 cms | [8 empty] | M² | 12000
| 10 x 360 cms | [8 empty] | M² | 5000
| suspension accessories and angle bead | [8 empty] | M² | 25000
02--06-00861 | Door closers Yale type or equivalent with all accessories | [8 empty] | No. | 100
02--06-00862 | Expansion joint beads made of stainless steel, 0.5mm thick | [8 empty] | M.L | 500
| Floor type | [8 empty] | M.L | 200
| Wall type | [8 empty] | M.L | 450
| Ceiling type | [8 empty] | M.L | 100
02-06-00863 | Special doors frames and door leaves different dimensions,with door handles (cylinder and bath). | [8 empty] | No. | 450
02-06-00864 | Anti static Vinyl tiles 120cm width, 3.5 mm thickness, with welding rods and fixing materials. | [8 empty] | M² | 500
02-06-00865 | Ceramic tiles 10 x 10 cm, 6mm thick, non-slip ceramic | [8 empty] | M² | 3500
02-06-00866 | Epoxy paints for walls | [8 empty] | Lit | 3000
02-06-00867 | Metal Lath 60 x 240 cm, weight 1.7 kg/m2 | [8 empty] | M² | 5000
02-06-00868 | diesel pump
| HP | r.p.m | Q m^3/hr | Hm | QTY
| 60-75 | 1450 | 200 | 60 | 5
02-06-00869 | electrical pump
| HP | r.p.m | Q m^3/hr | Hm | QTY
| 60-75 | 1450 | 200 | 60 | 5
02-06-00870 | NON-ION IC WATER SYSTEM | [8 empty] | 5
1-capasity:-3-4 m^3/hr
2-conductivity (mixing 0f + and - ) :- (0.1 - 0.5)MS
3-raw water input
main components
1-primary water tank (1m^3)
2-two duplex primary water pumps (6m^3/hr , 2.5bar)
3-three primary filters (25 micron)
4-four duplex water softener (cationic , 5m^3/hr)
5-secondary filters (5micron)
6-two duplex mixed bed deionizer (3-4m^3/hr
air handling unit (AHU)
| type of fulter | power (KW) | no of motor | type of air (AHU) |  | connecti size on (in-out) for each coil | air flow |  |  | water floow m^3/hr
|  |  |  | other type | in-line |  | for cooling | for heating |  | for cooling | for heating
02-06-00871 | type | 15 | 1 | _ | in line | 62.5mm | 8 12 | 8 12 |  | 102 | 45.5
02-06-00872 | type | 17 5.5 10 | 1 14 | _ | in line | in50mm out 50mm | 29153 | 29153 |  | 3581 | 1750
02-06-00873 | type | 4.1 11 | 1 | _ | in line | 62.5 | 5500/ 2200 | 5500/ 2200 |  | 13 | 13
02-06-00874 | type | 3.75 | 1 | _ | in line | in36mm out 36mm | 11864 | 11864 |  | 15.12 | 5.34
02-06-00875 | type | 7.5 | 1 | _ | in line | in50mm out 50mm | 26271 | 26271 |  | 21.36 | 6
02-06-00876 | type | 7.5 | 1 | _ | in line | in36mm out 36mm | 22881 | 22881 |  | 21.12 | 7.32
02-06-00877 | type | 7.5 | 1 | _ | in line | in50mm out 50mm | 23220 | 23220 |  | 39.48 | 17.96
02-06-00878 | type | 9.3 | 1 | _ | in line | in50mm out 50mm | 25424 | 25424 |  | 51.7 | 21
02-06-00879 | type | 5.625 | 1 | _ | in line | in50mm out 50mm | 15424 | 15424 |  | 31.32 | 12.81
02-06-00880 | type | 9.3 | 1 | _ | in line | in50mm out 50mm | 29153 | 29153 |  | 59.5 | 24.4
02-06-00881 | type | 2.25 | 1 | _ | in line | in50mm out 50mm | 8485 | 8485 |  | 14.7 | 7.2
02-06-00882 | MZ | 7.5 | 1 | _ | in-line |  | 30 | 30 |  | 40 | 40
02-06-00883 | normal | 10KW | 1 | _ | in-line | 2" inch | _ | _ |  | _ | _
02-06-00884 |  | 7.5 | 7 | X | _ | 3inch | X | X |  | X | X
02-06-00885 | _ | 4 | 1 | _ | in-line | _ | 30 | 30 |  | 40 | 40
air handling unit (AHU)
| type of fulter | power (KW) | no of motor | type of air (AHU) |  | connecti size on (in-out) for each coil | air flow |  |  | water floow m^3/hr
|  |  |  | other type | in-line |  | for cooling | for heating |  | for cooling | for heating
02-06-00886 | No.of AHU 15 N.B.S 35% | 18.5 | 1 |  | in line |  | 32.700 M^3/H | 32.700 M63/H |  | 655 L/Min | 107 L/Min
02-06-00887 | No.of AHU 19 N.B.S 80% |  | 55 | 1 | in line |  | 64.900 M^3/H | 64.900 M^3/H |  | 1202L/Min | 233 L/Min
fan coil unit
| no.of fan | no.of motor | type of fan coil unit |  |  |  | water temp. (In-out) | capacity (ton) |  | qnt.
|  |  | ground complete vertical |  | chiding horizontal
02-06-00888 | 2 | 1 | ground |  | _ |  | 9 12 | 2 |  | 52
02-06-00889 | 1 | 1 | _ |  | chiding horizontal |  | 70-11c | 3ton |  | 350
02-06-00890 | 1 | 1 | ground |  | _ |  | 70-11c | 2ton |  | 30
02-06-00891 | 1 | 1 | ground |  | _ |  | 70-11c | 2ton |  | 30
02-06-00892 | 1 | 1 | ground |  | _ |  | 70-11c | 2ton |  | 25
02-06-00893 | 3 | 1 | 10 |  | 18 |  | 6_12 | 40ton |  | 28
02-06-00894 | 4 | 20 | 10 |  | 10 |  | 10_12 | 2ton |  | 20
02-06-00895 | 2 | 2 | ground |  | _ |  | (5_10)c | 2ton |  | 100
02-06-00896 | cold stor | [9 empty] | 15
1-inside temperature (4-16C)
2-volume 20M^3
3-the cold store must be supplied with shade to from raining
4-ambiebient temperature 55C
5-the walls will be s and outs panel, the out side walls made from aluminum sheets at thickness 0.6mm and the inside walls made from aluminum sheet 0.6 mm,the out sid and the insid walls injected by polyethem with density 40KG/M^3, with thickness (100-120)mm
6-the floor made of jacker plane from aluminum
7-the door is hinged type
8-two cooling unit one work and the other stand by each unit is sufficient to keep inside temperature (4-16C)
9-the compressor is semi hermetic type
10-the cold store supplied with all the complete control (oil pressure,high-low pressure,thermostat,seloid valve pressure,high-low pressure,thermostat,seloid valve
02-06-00897 | refregrater | [9 empty] | 24
valume for refregrater 35foot^3
220V , 50HZ , 1phase
ferion:- R134
internal temperature ranging from +2to +6C
inside and out side material stainless steel
aolitle/visua/ alarm with battery , low alarm 0C , high alarm +10C
autamatic defrosting
out side thermometer or the door
7 day recorder
double compressor units for additionel/safety
removabe shalves inside
spar parts for 5 years
02-06-00898 | water ion exchenger | [9 empty] | 2
capacity:-20lit/hr
02-06-00899 | machine for sealing bottles of plastic & aluminum caps | [9 empty] | 4
02-06-00900 | centeral oxygen system | [9 empty] | 5
capasity:- 20 cylinder
1-tow stages (pressure)
a-first stage 160 :- 10Kg/cm^2
b- second stage 10 :- 4Kg/cm^2
right 10 clinder
lift 10 :- 4Kg/cm^2
| control system 24V | [9 empty] | 5
2-nitrous system 2 clinder
a-first stage 60 - 9Kg/cm^2
b- second stage 9 - 4Kg/cm^2
control system 24V
| 3-midical gas | [9 empty] | 5
normal & stand by
compress air oilless 2
5 start Kg/cm^2
7stop Kg/cm^2
reducing valv for pressure
filter system
pressure lin 4Kg/cm^2
bottle for air
| 4-centeral - vacum | [9 empty] | 5
valume line
1-bottle
2-check valve
working pressure
start pressure (vacum) 300 mmg
stop 500 mm /Kg
300 - 500 mm/Kg
02-06-00901 | softener | [9 empty] | 4
continuos softener supply as following
1-max.flow :- 1m^3/hr
2-resin - strong cationic resin sodium base
3-power supply 220V or 380V 50HZ
02-06-00902 | high tension switch gear | [9 empty] | 50
vaccum type 11KV input - 420V out put -3ph -800A with complete protection devise
02-06-00903 | softener | [9 empty] | 2
continuos softener supply as following
1-max.flow :- 1m^3/hr-cationic resin sodium base
2-power supply 220V 30W 50HZ
02-06-00904 | Absolute filter | [9 empty] | 150
size:- 505mm X 504mm x 150mm
dop - test :- 990997%
02-06-00905 | cold room 3X2 meter | [9 empty] | 4
02-06-00906 | PC computer pantum I I I | [9 empty] | 12
02-06-00907 | air purity for contamination portable tester to measure up to 0.3 microne particales . May be test by laser counter partical size | [7 empty] | 8
02-06-00908 | Elecri for tools and foodsc table top sterilizer , cold sterilizer with out change or detect in material for tools and foods | [7 empty] | 8
02-06-00909 | Table top dry hot air sterilizer | [7 empty] | 8
02-06-00910 | table top formation sterilizer | [7 empty] | 8
02-06-00911 | Atoclave poruos material 4ft3 | [7 empty] | 8
02-06-00912 | Plastic seeling machinc (with several role niylon) | [7 empty] | 8for equipment and (500) for rolles
02-06-00913 | 0.6 /1.2 kv single core cables , with flexible stranded circular copper conductors ,PVC .insulated and PCV sheathed
| Nomial cross section area mm2 | [7 empty] | Quantity
| 120 | [7 empty] | 20000 meter
| 240 | [7 empty] | 400000 meter
| 300 | [7 empty] | 120000 meter
| 3x50 +25 | [7 empty] | 60000 meter
02-06-00914 | Multy core cables , with flexible stranded copper conductor ,PVC insulated and PVC sheathed
| no. of cond.x cross section area | [7 empty] | Quantity (meters)
| 2x1.5 | [7 empty] | 20000
| 2x2.5 | [7 empty] | 20000
| 2x4 | [7 empty] | 10000
| 2x6 | [7 empty] | 6000
| 4x2.5 | [7 empty] | 10000
| 4x4 | [7 empty] | 20000
| 4x6 | [7 empty] | 4000
| 4x10 | [7 empty] | 4000
| 4x16 | [7 empty] | 4000
| 4x25 | [7 empty] | 4000
| 4x35 | [7 empty] | 4000
| 3x1.5 | [7 empty] | 4000
| 3x2.5 | [7 empty] | 4000
| 3x4 | [7 empty] | 4000
| 3x50 +25 | [7 empty] | 4000
| 3x70 +35 | [7 empty] | 4000
| 3x95 +50 | [7 empty] | 4000
| 3x120 +70 | [7 empty] | 4000
| 3x150 +70 | [7 empty] | 4000
| 3x185 +95 | [7 empty] | 4000
| 3x240 +120 | [7 empty] | 4000
| 3x300+150 | [7 empty] | 4000
02-06-00915 | Multicore cables with stranded copper conductors PVC insulated , steel wire armound and PVC sheathed
| 3x35 +16 | [7 empty] | 4000
| 3x50 +25 | [7 empty] | 4000
| 3x70 +35 | [7 empty] | 10000
| 3x95 +50 | [7 empty] | 4000
| 3x150 +70 | [7 empty] | 4000
| 3x185 +95 | [7 empty] | 4000
| 3x240 +120 | [7 empty] | 4000
| 3x300 +150 | [7 empty] | 4000
02-06-00916 | Cable terminals for cable sizes from 10 mm^2 to 300 mm^2 | [7 empty] | 2000PIECES FOR EACH SIZE
02-06-00917 | ELECTRICAL -HYDROLIC TERMINAL PRESS MACHINE | [7 empty] | 8
02-06-00918 | MANUAL - HYDROLIC TERMINAL PRESS MACHINE | [7 empty] | 8
02-06-00919 | EQUIPPED MOBILE LAB. FOR OCCUPATIONAL HEALTH AND SAFETY | [7 empty] | 40
02-06-00920 | EQUIPPED MOBILE LAB. Containing (noise level analyzer vibration analyzer ,condenser microphone ,triple microphone stand holder ,alpha numeric printer ,car counter ,electric generator ) | [7 empty] | 60
02-06-00921 | DO for cheking(BOD) , (ultra-dometer)
| instrument for determination of quantity of the mount of biological oxygen in water supplyment | [7 empty] | 16
extracts . Service system
02-06-00922 | electric refrigerator | [7 empty] | 10
02-06-00923 | kerosen refrigerator | [7 empty] | 5
02-06-00924 | vedio casset + CD | [7 empty] | 5
02-06-00925 | colour televsion (size : 24 note ) | [7 empty] | 5
02-06-00926 | telephone instrument | [7 empty] | 5
02-06-00927 | refregerated centrifuge | [7 empty] | 5
02-06-00928 | refregerated /heating water circulater (-10 TO 100 C) | [7 empty] | 10
02-06-00929 | freezer (-70) | [7 empty] | 10
02-06-00930 | refrigerator | [7 empty] | 10
02-06-00931 | microbiological safety cabinet and chemical hood and laminar air flow cabinet | [7 empty] | 5
02-06-00932 | phto copy machine | [7 empty] | 12
02-06-00933 | cuntarl station computer | [7 empty] | 5
| & terminal | [7 empty] | 60
02-06-00934 | cold room | [7 empty] | 5
02-06-00935 | office operatar with 100 lines | [7 empty] | 12
02-06-00936 | power amplifier (100W) | [7 empty] | 24units
model :- lbb 1103 (phillips)
required No./ 6 uints
02-06-00937 | air compressor | [7 empty] | 40
small for aeration of water sample (1-SL) sample valume
02-06-00938 | liquid nitrogen container of medium size (20 litres capacity) | [7 empty] | 8
02-06-00939 | softener
saadam medical city
| max flow:-90m^3/hr | [7 empty] | 20
| max flow:-70m^3/hr | [7 empty] | 5
| max flow:-50m^3/hr | [7 empty] | 5
general softener specification
dual/duplex system
resin:-strong cation
pressure vessel:high quality mild steel B.S 5500 working press 6 bar, internally protected by epoxy paint, eith manhole at tap.
valve:- amain multiport valve ,manual and automatic opreration
brine tank:-poly then with stainer and loose fit couer
operation:- flow counter supplied to intiat regeneration cycles
piping :- all piping including salt injeotion tubing is supplied
design row water condition
| total hardness |  | 289 to 610 PPM
| calcium |  | 84 to 323 PPM
| magnesium |  | 205 to 287 PPM
| other catios |  | 263 to 675 PPM
| bicar bonates |  | 160 to 159 PPM
| chlorides |  | 19 to 159 PPM
| totanions |  | 263 to 675 PPM
| chlorin |  | 1 to 2 cl PPM
02-06-00940 | ELECTRICAL OPERATED DOORS
| supply , install and operate electrical steel doors, double leaf (DIM . 180X210 CM + WITH 40X60 CM toughened veing glass.) 1.2MM steel plate for door and 2MM for frame WI epoxy painted finish. operating motors are two - way with (O) position and limit switch for fully open- fully close position , 220V , 50HZ . . Each pair to be interlocked | [7 empty] | 28 nos
air handling unit (AHU)
| type of filter | power (KW) | No.of motor | type of (AUH) |  | coucetion size (in-out)foreach coil |  | air-flow |  | QTY
|  |  |  | other type | in - line |  |  | for cooling | for heating
02-06-00941 | 2-no.meta- lic washable 50mm thiek 35%&bag 90% | 9 | 1 | _ | in-line mane | _ |  | 8500 | 8500 | 10
02-06-00942 | 2-no.meta- lic washable 50mm thiek 35%&bag 90% | 10 | 2 | _ | in-line mane | _ |  | 10650 | 10650 | 10
02-06-00943 | 2-no.meta- lic washable 50mm thiek 35%&bag 90% | 4 | 2 | _ | in-line single zone | _ |  | 2000 | 2000 | 10
02-06-00944 | 2-no metalic washable thich middle effic. F 35% of hepa. F 99.77% | 13 | 2 | _ | in-lne malti zone | _ |  | 8500 | 8500 | 10
02-06-00945 | 2-no.meta- lic washable type 50mm thich middle effici-f 35% & bag fill 90% effieic | 15 | 1 | _ | single zone | _ |  | 23370 | 23370 | 10
02-06-00946 | 2-no.meta- lic washable type 50mm thich middle effici-f 35% & bag fill 90% effieic | 25 | 1 | _ | single zone | _ |  | 32790 | 32790 | 10
02-06-00947 | requirements for simplex
| mobile radio system | [7 empty] | 10
mobile radio system compising the following main items is required to serve A service organization:-
1-two base station with dispatcher council to communicate with mobile and fixed station within 30 KM radius.(one to be used as spare unit).
2. High gain omni - directional antenna and feeder cable (100m) for the base station with the mask and all accessories.
3-10 fixed transceivers with directional antennas feeders and all others necessary accessories
4- 10 mobile vehicular transceivers with antennas feeders and all neccary accessories.
5-15hand uniys with necessary chargers and accessories
6-soare parts with avalue of 10% the total cost of equipment.
7-power supplie for the station and fixed units with U.P.S.
8-appropaiate test eqouipment>
9-full installation of the equipment should be part of the pffer and local training during installation.
10-on job trining should be offered
11-the frequency of operation will be allocated in the VHF frequency band (148-174MHZ).
12-the base sattion tx power should be between 10 and 25 watts and likewise for the fixed and mobile units. The handheld tx power should be between 3-5 watts.
13-warrenty one year from date of operation .
14-two years maintenance after period of warrenty.
15-training operaters and technicl staff on factory.
16- 2-complete sets of diagrams and manuals
| ype |  |  | head m | capasity L/min |  | suction m m |  | P(KW) | QTY
02-06-00948 | sewage submersible pump | _ |  | 22m | 400L/min |  | discharge 100 mm |  | 7.5KW | 10
02-06-00949 | water pump for sanitory HP2 | vertical |  | 15m | 50L/min |  | suction 32m m |  | 0.75KW | 10
02-06-00950 | water pump for sanitory HP3 | vertical |  | 20m | 100L/min |  | suction 40m m |  | 1.5kw | 10
02-06-00951 | chemical dosing pump for cooling tower | vertical |  | _ | 10kg/cm2 110cc/min |  | suction 2inch |  | 30watt | 10
02-06-00952 | circulating water pump HP | vertical |  | 29.7m | 320 L/m |  | _ |  | 2.2 | 10
02-06-00953 | submersibte pump SP | _ |  | 10m | 1000L/m |  | 100 mm |  | 3.7 | 10
02-06-00954 | eng camera
| item No. | descrription | [6 empty] | quantity (state unit)
| 1 | betacam sp camcorder camera PVW-D 30 PF | [6 empty] | 10
| 2 | play back adaptor VA-300P | [6 empty] | 10
| 3 | rechargable NI - CD battery | [6 empty] | 48
| 4 | AC adapter AC - 550 CE | [6 empty] | 10
| 5 | battry case DC - 520 | [6 empty] | 10
| 6 | chest pad CAC - 4 | [6 empty] | 10
| 7 | microphone holder CAC 12 | [6 empty] | 10
| 8 | battry charger BC - 1 wdce | [6 empty] | 10
| 9 | UHF wireless microphone wrt - 830 a with UHF wirless receiver (complete) | [6 empty] | 10
| 10 | betacam sp 20 min. metaltape | [6 empty] | 300
| 11 | betacam SP 30 min. metaltape | [6 empty] | 300
| 12 | tripod - vision 10 lf complete set | [6 empty] | 10
02-06-00955 | A/B roll editing system with DFS - 500 P (digital effects)
| item No. | complete description of item | [6 empty] | quantity (state unit)
| 1 | betacam sp recorder | [6 empty] | 10
| 2 | betacam sp player | [6 empty] | 10
| 3 | editing control unit | [6 empty] | 10
| 4 | vtr interf ace | [6 empty] | 10
| 5 | serial switche interf ACE | [6 empty] | 10
| 6 | B/W data display | [6 empty] | 10
| 7 | bme switcher | [6 empty] | 10
| 8 | serial switche interf ACE | [6 empty] | 10
| 9 | color monitor | [6 empty] | 18
| 10 | color monitor | [6 empty] | 10
| 11 | dubbing cable (12 pin) | [6 empty] | 24
| 12 | remote control cable | [6 empty] | 18
| 13 | audio mixer | [6 empty] | 10
| 14 | audio amplifire | [6 empty] | 10
| 15 | speaker (3 WAY) | [6 empty] | pair
| 16 | desk & pack mount metal | [6 empty] | complete
| 17 | main power output with AC out let box | [6 empty] | 10
| 18 | bet acam sp plater | [6 empty] | 10
02-06-00956 | cold stor | [7 empty] | 10
internal temp. raning form (-20c) to (+10C) at the folowing amdient conditions
summer : DBT 45C
winter : DBT _ 5C
internal volum not less than 32 cubic meters
referigeration system two indepent refrigeration with an automatic altermatorm clock timer furnished to automatically reverse the sequence of operation of the two systems , and if one system be unable for any reason to maintain the required temp. the second system shall automatically cut in
system shall operate from single - phase 220V , 50HZ or 3phase , 4wire 380v
02-06-00957 | AMBULANCE | [7 empty] | 600
PARTITION
BETWEEN DRIVER'S COMPARTMENT AND PATIENT’S COMPARTMENT FULL COVERAGE PANEL MADE OF STURDY MATERIAL (PRESS WOOD IS NOT TO BE USED) WITH SMOOTH SURFACE AT BOTH SIDE.
PARTITION WINDOW
LARGE, DOUBLE SLIDING SAFETY GLASS CENTRAL WINDOW
PATIENT'S COMPARTMENT
THE PATIENT'S COMPARTMENT IS TO BE FULLY INSULATED.
ROOF HEIGHT
INSIDE HEIGHT NOT LESS THAN 1500MM WITHOUT THE THICKNESS AND REINFORCEMENT.
FLOORING
HIGH QUALITY FLOORING MATERIAL CEMENTED TO A SUITABLE TYPE OF WOOD WITH ALUMINUM MOLDING.
MEDICINE CABINETS
THE LEFT WALL OF THE PATIENT’S COMPARTMENT IS TO BE PARTITIONED INTO ENCLOSED STORAGE CABINETRY. COMPARTMENT SPACE AND SHELF SPACE TO BE CONVENIENTLY LOCATED FOR MEDICAL SUPPLIES, DEVICES AND INSTALLED SYSTEM AD APPLICABLE FOR THE SERVICE INTENDED. CABINETS ARE TO BE EASILY OPENED WITH SHATTERED-PROOF TRANSPARENT SLIDING DOOR THE WALL IS TO BE NOT MORE THAN 30 INCHES HIGH. REMOVAL OF CABINET IS TO BE EASY TO FACILITATE BODY REPAIR IN CASE OF AN ACCIDENT.
TECHNICIAN SEAT - FRONT
PROVISION OF A TECHNICIAN SEAT AT THE FRONT OF THE PATIENT'S COMPARTMENT.
TECHNICIAN SEAT-REAR
PROVISION OF A TECHNICIAN SEAT AT THE FOOT OF THE PATIENT'S ON THE RIGHT END SIDE.
INSIDE LIGHTING SYSTEM
THE PATIENT'S COMPARTMENT ELECTRICAL SYSTEM IS TO BE SEPARATED FROM THE TRUCK.
IDENTIFICATION
THE AMBULANCE IS TO BE IDENTIFIED AS FOLLOWS:-
IT IS TO BE PAINTED CLEAR WHITE
- FOR DECALS FOR THE WORD "AMBULANCE", AND A RED CRESCENT IN ARABIC ONE ON EACH SIDE, ONE ON THE REAR, AND ONE ON THE FRONT
RESUSCITATION EQUIPMENT
- TWO OXYGEN BOTTLES, EACH OF 500 LITTER CAPACITY SECURED WITHIN THE LEFT WALL CABINETRY.
- TWO SPARE OXYGEN BOTTLES OF 500 LITTER CAPACITY IN STOWAGE CABIN.
- ONE SET OF ENGLISH BULL NOSE VALVE YOKE, PRESSURE REGULATOR WITH GAUGE FLOW METER AND HUMIDIFIER BOTTLE.
- THREE OXYGEN MASKS, ONE FOR EACH ADULT CHILD AND INFANT.
- THREE PLASTIC NASAL CANNULAS, TWO ADULT AND ONE CHILD.
- FOUR OXYGEN CATHETERS, TWO OF EACH NO.10F.
ONE MOUTH TO MOUTH VENTILATION MASK
| CYLINDER KEY | [7 empty] | 1 FOR EACH
| OXYGEN FLOW METER /REGULATOR | [7 empty] | 1 FOR EACH
| HUMIDIFIER | [7 empty] | 1 FOR EACH
PORTABLE OXYGEN KIT
ONE PORTABLE OXYGEN KIT COMPETE WITH REGULATOR AND SUPPLIES.
| RESUSCITATOR COMPLETE WITH CYLINDER. | [7 empty] | 1 FOR EACH
| RESTRAINING STRAP FOR RESUSCITATOR. | [7 empty] | 1 FOR EACH
SUCTION SYSTEM
ONE VACUUM APPARATUS INCLUDING AN ELECTRIC DRIVEN PUMP with rechargable battery
FIRST AID EQUIPMENT
A BOX IS TO BE PROVIDED CONTAINING THE FOLLOWING:-
TWENTY PRE- LOCALIZED PADS
TWELVE COMPRESSIVE BANDAGES
- FOUR 10CM ELASTIC STRIPS.
- SIX GAUZE BANDEAUS, THREE OF 75MM AND THREE OF 150MM.
- TWENTY GAUZE PADS 10CM BY 10CM, INDIVIDUALLY WRAPPED.
- TWO 5CM ANTI-ALLERGIC ROLLS OF ADHESIVE TAPE.
FIFTEEN TONGUE DEPRESSORS INDIVIDUALLY WRAPPED.
- ONE 100 ML BOTTLE CONTAINING CHLOREXIDINE BASE DISINFECTANT.
AIR SPLINTS
ONE SET OF AIR SPLINT FOR EACH OF THE UPPER AND lower LIMBS.
STRETCHER
WHEEL STRETCHER WITH ADJUSTABLE BACK AND FOOT RESTS WITH SIDE HANDLES, COMPLETE WITH MATTRESS AND COVER.
SPARE STRETCHER
FOLDING COLLAPSIBLE STRETCHER WITH SUPPORTING SPREADER BARS AND VINYL COATED NYLON FABRIC.
REAR BUMPER STEP
A- REAR BUMPER STEP IS TO BE INSTALLED OVER THE REAR BUMPER.
BOTTLE HOOKS
BOTTLE HOOKS ARE TO BE INSTALLED ON THE ROOF TO HOLD FLUID AND BLOOD TRANSFUSION BOTTLES.
SPARE STRETCHER HOLDER
SPECIAL HOOKS ON WALL AND ROOF ARE TO BE PROVIDED TO HOLD SPARE STRETCHER WHEN REQUIRED.
EXHAUST-VENTILATOR FAN
ROOF MOUNTED DOUBLE ACTING EXH-VENT FAN IS TO BE INSTALLED.
REAR BUMPER STEP
A REAR BUMPER STEP IS TO BE INSTALLED OVER THE REAR BUMPER.
BOTTLE HOOKS
BOTTLE HOOKS ARE TO BE INSTALLED ON THE ROOF TO HOLD FLUID AND BLOOD TRANSFUSION BOTTLES .
ANTENNA
INSTALLATION OF RADIO ANTENNA IN EACH AMBULANCE AT THE ROOF.
WIRELESS EQUIPMENT: EACH AMBULANCE EQUIPPED WITH RADIO (WIRELESS COMMUNICATION DEVICE).
SPECIFICATIONS FOR AMBULANCES
BASIC VEHICLE
ENGINE: PETROL ENGINE WATER COOLED .
TRANSMISSION: MANUAL OR AUTOMATIC.
AXLE: 4X4 wheel driver
STEERING :POWER STEERING LEFT HAND DRIVE.
SUSPENSION : HEAVY DUTY.
COOLING SYSTEM: HEAVY DUTY.
ELECTRICAL SYSTEM: 12 VOLTS WITH HEAVY DUTY ALTERNATOR AND BATTERY.
AIR CONDITIONING SYSTEM: AIR-CONDITIONER AND HEATER FOR BOTH DRIVER AND PATIENT COMPARTMENTS.
SIDE DOOR: SIDE DOOR AT THE RIGHT SIDE.
BACK DOORS: TWO PANEL DOORS OPENABLE TO THE SIDES.
INSTRUMENT PANEL: WITH METRIC GAUGES and ODOMETER.
MIRRORS: ONE INSIDE and TWO OUTSIDE REAR VIEW.
TIRES :HIGH QUALITY INCLUDING SPARE.
-WARNING EQUIPMENT: SIREN WITH SPEAKER AND BEACON OF THE FOLLOWING TYPES:
-ELECTRONIC SIREN WITH PUBLIC ADDRESS SYSTEM OF 100WATTS OUT-PUT POWER.
BEACON : TWO REVOLVING DOME TYPE BEACONS LONGITUDINAL A LONG THE WIDTH ON THE FRONT ROOF
-SPEAKER: 100 WATTS SPEAKER INSTALLED INSIDE ENGINE COMPARTMENT.
-ACCESSORIES:
AUTO JACK WITH HANDLE and WHEEL WRENCH.
TOOL KIT BAG.
HAZARD WARNING TRIANGLE
FIRE EXTINGUISHER.
-MISCELLANEOUS: THE FOLLOWING IS TO BE SUBMITTED TWO WEEKS AFTER ORDER CONFIGURATION:
-WORKSHOP MANUALS (2 COPIES IN ENGLISH).
-SPARE PARTS CATALOGUES (2 COPIES IN ENGLISH).
-RECOMMENDED SPARE PARTS LIST (DETAILS OF THE LIST ARE TO BE AGREED UPON).
FAST MOVING PARTS for EACH VEHICLE.
- TRAINING FOR 3 ENGINEERS.
optional rquipments schedule ambulance
| VACUUM MATTERS WITH CARRYING HANDLES. | [7 empty] | 1 FOR EACH
| PUMP FOR VACUUM MATTRESS | [7 empty] | 1 FOR EACH
| FOLDING STRETCHER | [7 empty] | 1 FOR EACH
| INFLATABLE SPLINTS, SET OF 4 IN WALLET. | [7 empty] | 1 FOR EACH
| ANALGESIC UNIT. | [7 empty] | 1 FOR EACH
| NITRONOX CYLINDER (LIGHT WEIGHT) | [7 empty] | 1 FOR EACH
| URINAL, MALE. | [7 empty] | 1 FOR EACH
| URINAL, FEMALE. | [7 empty] | 1 FOR EACH
| ORTHOPEDIC SCOOP STRETCHER | [7 empty] | 1 FOR EACH
| BRACKETS FOR SCOOP STRETCHER. | [7 empty] | 1 FOR EACH
| HEAPED AND HARDNESS SET FOR SCOOP STRETCHER. | [7 empty] | 1 FOR EACH
| ASPIRATOR, MANUAL | [7 empty] | 1 FOR EACH
| AMBULANCE CHAIR | [7 empty] | 1 FOR EACH
| BRACKET FOR AMBULANCE CHAIR | [7 empty] | 1 FOR EACH
| FIRST AID KIT COMPLETE WITH CASE. | [7 empty] | 1 FOR EACH
| PENLIGHT | [7 empty] | 1 FOR EACH
| BEDPAN | [7 empty] | 1 FOR EACH
| ANEROID SPHYGMOMANOMETER | [7 empty] | 2 FOR EACH
| STETHOSCOPE. | [7 empty] | 2 FOR EACH
| OTOSCOPE. | [7 empty] | 1 FOR EACH
| THOUGHT CUT SCISSORS. | [7 empty] | 1 FOR EACH
| SEMI AUTOMATIC DEFIBRILLATOR /MONITOR | [7 empty] | 1 FOR EACH
| SECURING DEVICE FOR DEFIBRILLATOR /MONITOR | [7 empty] | 1 FOR EACH
| ARTERY FORCEPS (SPENCER WELLS) | [7 empty] | 1 FOR EACH
| DISSECTING FORCEPS, PLAIN | [7 empty] | 1 FOR EACH
| SCISSORS BANDAGE. | [7 empty] | 1 FOR EACH
| THERMOMETER | [7 empty] | 1 FOR EACH
| NON WOVEN ACRYLIC BLANKET 60"X80" APPROX. | [7 empty] | 1 FOR EACH
| CELLAR BLANKET UNBLEACHED 60"X80" APPROX. | [7 empty] | 2 FOR EACH
| FOAM PILLOW, PCV COVERED | [7 empty] | 2 FOR EACH
| VACUUM FLASK STAINLESS STEEL 1 LITTER. | [7 empty] | 2 FOR EACH
| RESTRAINING STRAP FOR VACUUM FLASKS | [7 empty] | 1 FOR EACH
| OXYGEN CYLINDER, BULL NOSE (SIZE F) | [7 empty] | 1 FOR EACH
| OXYGEN FACE MASK | [7 empty] | 1 FOR EACH
| GREEN BUBBLE 30 FOOT ROLL | [7 empty] | 2 FOR EACH
02-06-00958 | freezer -80 | [7 empty] | 18
1-horzintal type heavy insulation or vertical type
2-temp . Range 0 - (-80c)
3-double compressor heavy duty with fan cooling system
4-alarm - system
5-thermal - control - system with multi - indicators
6-parttion and baskets for samples
7-size 16-20 cubic feet
02-06-00959 | freezer -20 | [7 empty] | 16
1-horzintal type heavy insulation or vertical type
2-temp . Range 0 - (-80c)
3-single compressor heavy duty with fan cooling system
4-alarm - system
5-thermal - control - system with multi - indicators
6-parttion and baskets for samples
7-size 16-20 cubic feet
02-06-00960 | lab - refrigrator | [7 empty] | 14
1-14cupic feet type with lock for freezing & refrigrater
2- double door one for freezer ( - 10c) & one for refrigrater (4 - 8c )
3- freezer :- parttions 2 or 3 with drawers for freezing samples ( _10c)
4-refrigrater (4 - 8c) with parttions (4 - 5) and drawer supplied with (D R I N) out let for washing and sterlization
5- heavy duty compressor with fan for cooling purposes
6-refergerater and freez have thermometer fixed on the front side
7- refrigerater have atomatic defrost system
8-220v/50HZ/ 1 PH
9- R134
02-06-00961 | blood bank coold store | [7 empty] | 10
inside temp from 1C to 6C at the following ambient conditions
summer : DBT 50 C
WBT 25 C
winter : DBT 1C
WBT -3 C
Internal volume : not less than 50 cubic meters
A) construct ion :
1- cold stores shall be shipped in knock – down sections to re-erect
2- cabinet interior shall be made of heavy corrosion proof aluminum, floor made of heavy gauge anti – slip aluminum
3- cabinet exterior shall be made of aluminum , coated with a white weather proof coating to make it suitable for out-door installation
4-In sultan shall be sufficient to maintain the specified internal temperature in the specified ambient condition but shall be not less than 10 cm of polyurethane
5- Door shall be constructed of aluminum & shall have an external lock with keys. Door handle can be operated from inside & outside. Low voltage heater wire strip with electrical control shall be provided. Apish-button shall be fitted inside to sound an alarm in case of person is trapped
6- light- weight shade to protect the cabinet from rain & sun to be fitted on top of it. Shape size & material of shade shall be suggested by the tendered
7- external dial thermometer must be provided
8- Audio & visual alarm for high temperature must be fitted
9- Sufficient internal lighting automatically switches on when door opens
10- air curtain by the door operates automatically when door opens
11- Shelves shall be made of strong galvanized steel positioned on all sides shelves shall be grid type accommodating heavy blood bank refrigerator drawers full of blood pints when stored in the cold room and carried to or from it 3 raws of shelves
12- (7 days recorder
B) .REFRIGERATION SYSTEM
Two independent refrigeration system shall be installed each being capable to maintain the required internal temp. at the specified ambient conditions an automatic alternator clock timer shall be furnished to automatically reverse the sequence of operation of the two systems to assure even wear , and if one system be unable for any reason to maintain the required temp. the second system shall automatically cut- in . Visual indication of the operation & faults of the system shall be shown on the control panel. Capacity &type of compressor used shall be mentioned in the offer . the entire system shall utilize heavy duty refrigeration copper tubing , no aluminitium or steel tubing to be used . evaporator fins shall be anticorrosion type . automatic electrical defrost with pipes for drain water must provided .use R12 or R502
C) Electrical system
System shall operate from single – phase , 220V, 50 HZ, supply or from 3 pH , 4 wire , 380 V
D) Spar parts 5 years
02-06-00962 | Developed operating washing tube | [7 empty] | 10
02-06-00963 | PIIII or PIII with accessires and read - write CD - drive | [7 empty] | 60
| printer EPSON LQ - 2180 | [7 empty] | 46
| laser - printer 10 L | [7 empty] | 14
| page printer | [7 empty] | 5
| U.P.S | [7 empty] | 62
| reglater power 10AMP | [7 empty] | 66
| reglater power 20AMP | [7 empty] | 5
| white board | [7 empty] | 5
| over head pros | [7 empty] | 5
| sidlater | [7 empty] | 5
| disk 3.5 | [7 empty] | 200
| laser - disk | [7 empty] | 20
02-06-00964 | intercom system
| central digital intercom system comprise of one master station with special faeilities and 100 or 50 slave station, the system evakle each slave station to communicall with other slave station and with the master station | [7 empty] | 60 for system with 200 slave station
| _ installation the systems on siltes | [7 empty] | 200 for system with 100 slane stations
_ one year earranty and two year maintenaes
_ complete sets of drawing and manuel and catalogues
_ spetionl too kit for each system
_ training coerse 4 engineers for 3 weeks , on factory
_ spare parts for two years
02-06-00965 | clock system | [7 empty] | 200
central clock system contoins:-
| a- master clock | [7 empty] | 1
| b- single face slave clock | [7 empty] | 100
| c- double face slave clock | [7 empty] | 30
| d- special clock for operating theater | [7 empty] | 8
| c-time machine | [7 empty] | 2
one year waranty , two year maintenaes, installation complet set of manuals and catalogies and drawing spare parts for two years
training coerse on factory for 3 engineers for 3 weeks
02-06-00966 | electrical switchs and souket
| 1-single switch 220V /up to 15A - B.5 | [7 empty] | 27200
| 2-double switch 220V / up to 15 A - B.5 | [7 empty] | 6560
| 3-frible switch 220V / up to 15 A - B.5 | [7 empty] | 13120
| 4-four way switch 220V / up to 15 A - B.5 | [7 empty] | 2400
| 5- mercury switch 220V / up to 15 A - B.5 | [7 empty] | 1000
| 6- electrecal out let 220220V / up to 13 A - B.5 13A - B.S | [7 empty] | 31420
| 7- electrecal out let 220220V / up to 15 A - B.5 13A - B.S | [7 empty] | 16900
02-06-00967 | over loads
| NO. of poles | NO. of phaes | current A | Voltage | Qty
| 3P | 3Q | 0 - 35 | 220V | 440
| 3P | 3Q | 5 40 | 220V | 320
| 3P | 3Q | 3 60 | 380V | 860
| 3P | 3Q | 80-200 | 380V | 80
| 3P | 3Q | 30 - 90 | 380V | 200
| 3P | 3Q | 20 - 80 | 380V | 1000
| 3P | 3Q | 2 15 | 380V | 320
| 3P | 3Q | 200-500 |  | 180
02-06-00968 | contactors
| NO. of poles | NO. of phaes | No. of auxiliang contact | Voltage of coil | Voltage | current A |  | Qty
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 10A |  | 120
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 16A |  | 100
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 20A |  | 100
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 25A |  | 60
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 30A |  | 420
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 40A |  | 290
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 50A |  | 160
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 60A |  | 440
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 80A |  | 240
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 100A |  | 258
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 250A |  | 100
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 400A |  | 15
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 1000A |  | 40