## 02-06-00669
02-06-00669 | air washer schedual
| no. req | type | location | summer |  |  | winter (heating coil) | [9 empty] | blower |  |  |  |  | circulation water pump kw | electrical characteristic |  |  | filter
|  |  |  | amb. Temp wb c | press. Nozzle m.w.g | water circulation lit/min | grand total heat kcal/hr | air temp c |  |  |  | water temp.c |  | water qty lit/min | no of fins /25mm | no of rows | blower type | total air qty m/hr | face velocity m3/sec | total static pressure mm w g | motor kw |  | volt | phase | hertz | type | thickness mm
[8 empty] | in |  | out |  | in | out
[8 empty] | DB | WB | DB | WB
| 200 | double bank spray | block c on the roof | 26 | 25 | 750 | 431680 | 1.5 | 0.8 | 33.5 | 5.5 | 82 | 71 | 650 | 8 | 2 | centrifugal aerofoil | 121380 | 2.5 | 22 | 18 | 7.5 | 380 | 3 | 50 | metalic cleanable | 50