## 0001-01690
SECTION 1: SEWAGE WORK REQUIREMNTS
SECTION1-1: SEWAGE WORK REQUIREMNTS FOR RUSTMIYA SEWAGE TREATMENT PLANT (1,2,3)
SECTION : 1-1-1 : 12 -3.3 KW sub-stations
CODE NO. | DESCRIPTION | QTY
03-01-00001 | 12 k.v. sub-station consist of: | 1
a-1250A isolater (vacuum type) with inter lock and automatec change over 2-no
b-1250A circuit breaker (vacuum) drawable with full protaction(over current-earth full
…..) for cable feeder . 2-no
c-bus-tie for current tranformer (c-t)(b-t) metaring 1-no
note:with out using charger.
03-01-00002 | 12 k.v. sub-station consist of : | 4
a-630A incoming c.b. (vacuum) drawable with full cable feeder protaction 2-no
b-630A transformer feeder (1600kva) drawable (vacuum) -full protaction 2-no
c-bus-tie (C-T)(B-T)(metaring) 1-no
d-alcaline battary with charger . 1-no
note:all C.B.s motarized
03-01-00003 | 12 k.v. sub-station consist of : | 1
a- 630A transformer feeder C.B. (vacuum) motorized drawable(3500kva) 2-no
with inter-lock and full protaction .
03-01-00004 | 3.3 k.v. sub-station consist of : | 1
a-3.3 k.v. 1250A incoming drawable (vacuum) C.B. with inter lock , motorized,
and full protection for bus-bar feeder . 2-no
b-3.3 k.v. 1250A bus-section drawable (vacuum) motorized C.B . With inter lock 2-no
c-3.3 k.v. 630A C.B. cable feeder (vacuum) drawable motorized with full protection
(C.T),(B.T), and metering 5-no
d-3.3 k.v. power factor improving compact unit C.B 630A with 5-stage complet control
| from(0--1000kvr).,protaction ,metering 1-no | 1
| e-alkaline battry charging unit . 1-no | 1
note:all C.B.s and coupliers are motorized with full protaction,and use gas proof
meters and relaies.
SECTION : 1-1-2: 3.3 kv sub-station
code no | description | q y t | unit pr.
code no | description | QTY
03-01-00005 | a-400A 3.3kv (vacuum) C.B. drawable with full protaction for transformer feeder (400kva) | 5
| b 400 A , 3.3KV. = = isolator = motorized for incoming and out going 2-no | 2
SECTION : 1-1-3: 3.3 kv sub-station consist of:
code no | description | QTY
03-01-00006 | a-630A C.B. (vacuum),motorized,full protaction for incoming drawable 2-no | 2
. | b-= = = for bus-section with inter-lock = 2-no | 2
. | c-400A = = = ,full protaction for cable feeder = 7-no | 7
. | d-400A = = = = = = generator = =with inter-koc 2-no | 2
. | e-alcalin battries with charger 1-no | 1
SECTION : 1-1-4: 3.3 kv sub-station consist of:
code no | description of 3.3 kv sub-station consist of: | q y t
03-01-00007 | a-400A C.B. (vacuum),motorized,full protaction for incoming fixed. 2-no | 1
b-= = = for bus-section with inter-lock = 2-no
c-100A = = = ,full protaction for transforme feeder (100kva) 1-no
d-400A-380v-MCCB-with contactor+over lode+gas proof metering+push potums 1-no
e-using C.T ,B.T s for control and protaction .
SECTION : 1-1-5: low voltage control penal
code no | description | q y t
03-01-00008 | 15kw motor starters (control penal) consist of: | 1
a-control penal (2mm)with epoxy coated ,with drawable cubicals(70) starter ,the penal
have tow air-circuit breakers(2500A-3-P-380V) drawabile type with full protaction
,gas proof meters.
b-each drawable starter have( manual starter + contactor (220v-ac3-80A)+solid state
over-lode coated with epoxy+currnt CT + gas proof amper meter + selecter switch
with 3-mode(0-A-M).+ push putomes), each cubical have front isolater & lambs.
the penal have bus-bar zoon & bus-bar coated with epoxy with cable zoon
each cubical have space not less (50-30-30)cm
c-the control of the starters in automatic position don by mecanical cam switch work
to operated the starters from 50% up to 100% ,on pirode with 12 hour .
d-using isolating transformer for conttrol 380------220v.
note:the penal have side & back slots to coolent .
using isolater for each 7 starters ,using multi-function protaction relay
the penal digsin to work in 55c ,
03-01-00009 | b-400A isolater C.B with inter lock 2-no | 2
03-01-00010 | c-100A C.B fixed motorized,full protaction for transformer (100kva). 1-no | 1
03-01-00011 | d-400A 380V MCCB with cotactor - over lode ,metaring for low voltage 1-no | 1
e-using (BT,CT)protaction with out charger
SECTION : 1-1-6: 3.3 kv motor starters
code no | description | q y t
03-010012 | 3.3kv motor control penal consist of: | 2
a-starter to start four 3.3kv motors (250-160-160-90)kw,(slip-ring type),using vacuum
contactor (400A-110VDC for coil) to feed the staters with full protaction(isolater fuse
+h.r.c fuses+over current + under voltage +phase lag.+earth fult+C.T&B.T)
b-four air - resistant units with complite 4-stages contactors&timers(off delay-p.v.c.)
type, to be connected with rotor of slip-ring motor,& p.t.c protoction.
note:using 2 mm plate,& nema size,no need to use charger using BT&CT
03-01-0013 | b-400A transformer feeder (400kva) & cable feeder drawable (vacuum) -full protaction
with (C.T)&(B.T) ,gas proof metering. 7-no
c-400A C.B for generator with full protaction inter lock with incoming 2-no
d-630A = = bus section with inter-lock 2-no
e-alcaline battry charger 1-no
03-01-0014 | 3.3 k.v. sub-station consist of : | 1
a-400A cable feeder C.B. (vacuum) motorized fixed 2-no
with inter-lock and full protaction .
b-400A isolater C.B with inter lock 2-no
c-100A C.B fixed motorized,full protaction for transformer (100kva). 1-no
d-400A 380V MCCB with cotactor - over lode ,metaring for low voltage 1-no
e-using (BT,CT)protaction with out charger
SECTION :1-1-7: low voltage control penal
code no | description | q y t
03-01-0015 | 7.5kw motor starters (control penal) consist of: | 1
a-control penal (2mm)with epoxy coated ,with drawable cubicals(70) starter ,the penal
have tow air-circuit breakers(2500A-3-P-380V) drawabile type with full protaction
,gas proof meters.
b-each drawable starter have( manual starter + contactor (220v-ac3-32A)+solid state
over-lode coated with epoxy+currnt CT + gas proof amper meter + selecter switch
with 3-mode(0-A-M).+ push putomes), each cubical have front isolater & lambs.
the penal have bus-bar zoon & bus-bar coated with epoxy with cable zoon
each cubical have space not less (50-25-20)cm
c-the control of the starters in automatic position don by mecanical cam switch work
to operated the starters from 50% up to 100% ,on pirode with 12 hour .
d-using isolating transformer for conttrol 380------220v.
note:the penal have side & back slots to coolent .
using isolater for each 7 starters ,using multi-function protaction relay
the penal digsin to work in 55c ,
with inter-lock and full protraction .
b-400A isolater C.B with inter lock 2-no
c-100A C.B fixed motorized,full protaction for transformer (100kva). 1-no
d-400A 380V MCCB with cotactor - over lode ,metaring for low voltage 1-no
e-using (BT,CT)protaction with out charger
code no | description | q y t
03-01-0016 | 37kw motor starters (control penal) consist of: | 1
a-control penal (2mm)with epoxy coated ,with drawable cubicals(20) starter ,the penal
have tow air-circuit breakers(2500A-3-P-380V) drawabile type with full protaction
,gas proof meters.
b-auto-transformer starter with 3-stages using 3-no 180A contactor+electronic
over-lode coated with epoxy+currnt CT + gas proof amper meter + selecter switch
with 3-mode(0-A-M).+ push putomes), each cubical have front isolater & lambs.
the penal have bus-bar zoon & bus-bar coated with epoxy with cable zoon
each cubical have space not less (70-50-40)cm with thermel protaction sensor in TR
c-the control of the starters in automatic position don by mecanical cam switch work
to operated the starters from 50% up to 100% ,on pirode with 12 hour .
d-using isolating transformer for conttrol 380------220v.
note:the penal have side & back slots to coolent .
using isolater for each 2 starters ,using multi-function protaction relay
the penal digsin to work in 55c ,
with inter-lock and full protraction .
b-400A isolater C.B with inter lock 2-no
c-100A C.B fixed motorized,full protaction for transformer (100kva). 1-no
d-400A 380V MCCB with cotactor - over lode ,metaring for low voltage 1-no
e-using (BT,CT)protaction with out charger
SECTION :1-1-8: different electrical materials
code no. | description of | q t y
1- liqiud for rotor startor in slip-ring motors (vectrohm type) with solution ,catloges
03-01-0017 | R-25 | 15
03-01-0018 | R-65 | 10
03-01-0019 | R-120 | 10
03-01-0020 | R-200 | 15
03-01-0021 | R-200P | 5
note:with spare solution .
03-01-0022 | 2-off-delay timer punumatic type ( cuttler hamer) 0-30sec. +control contactor 220v | 100
or equevlint set.
03-01-0023 | 3-off-delay electronic timers 0---30 min. | 50
03-01-0024 | 4-on- = = = = = | 50
03-01-0025 | 5-thermel over-lode relay 0.6---------1A | 50
03-01-0026 | 6- = = = = 1 ---------1.6A | 50
03-01-0027 | 7- = = = = 1.6---------2.5A | 50
03-01-0028 | 8- = = = = 2.5--------4A | 30
03-01-0029 | 9- = = = = 4----------6A | 50
03-01-0030 | 10- =============== 6--------13A | 30
03-01-0031 | 11- =============== 13-------18A | 60
03-01-0032 | 12- =============== 18--------25A | 30
03-01-0033 | 13- ================= 25-------32A | 60
03-01-0034 | 14- ================= 32---------50A | 30
03-01-0035 | 15- ================ 50---------80A | 30
03-01-0036 | 16- ================ 65---------100A | 30
03-01-0037 | 17- ================ 90----------150A | 30
03-01-0038 | 18- ================ 130---------220A | 20
03-01-0039 | 19-================ 200---------320A | 20
03-01-0040 | 20- ================ 300--------500A | 20
03-01-0041 | 21- ================ 400--------600A | 20
03-01-0042 | 22- thermistor short - circuit detection 220v - 50hz - with (p.t.c) sensors (90-110c) | 50
23- 3-p reversing contactor breakers with thermel-magnatic protaction
03-01-0043 | 4-KW | 20
03-01-0044 | 9-KW | 50
03-01-0045 | 15-KW | 50
03-01-0046 | 30-KW | 30
03-01-0047 | 0.25KW | 50
03-01-0048 | 0.37KW | 50
03-01-0049 | 0.55KW | 50
03-01-0050 | 0.75KW | 50
03-01-0051 | 1.1KW | 50
03-01-0052 | 1.5KW | 30
03-01-0053 | 2.2KW | 30
03-01-0054 | 24-spring return push buttons (different colors ) | 300
03-01-0055 | 25-start--stop = = | 100
03-01-0056 | 26-voltage tester cam-switch | 30
03-01-0057 | 27-selector switch 3-mode (0-1-2) | 200
03-01-0058 | 28-graphit coper prushes with alamnum wire & termenels,(30*45*60)mm | 250
03-01-0059 | 29-puls timer electronic 220v 50hz on time 1s--10h,off time 1s--10h | 50
SECTION1-1-9 :REQUIREMENTS FOR f-1 pumping station
code no. | description | qty
03-01-0060 | 1-center fugure pumps q=5400m3/h,h=15.65M,585rpm, | 3
type spyv700-750as or equivlent with complet set of virtical shaft from drive motor
to pumps & brackets
03-01-0061 | 2-slip-ring motor 3-ph,380v,50hz,295kw,585rpm,class f ,the slip ring are saparated | 3
from stater ,ip=23,with p.t.c.,the coleent fan fixed on rotor shaft,brush left divce
03-01-0062 | 3-10--stages rotory oil - resistant starter for rotor starting ,with full protaction | 3
03-01-0063 | 4-control penal with two incoming air circuit breaker 3p,380v&n, 2500A,(one for gen- | 1
rator the second for incoming ) with spicfication:
a-have bus-bar zoon&cable zoon.
b-using MCCB for motor (s.c) protaction.
c-using AC3 contactor 1000A for stater feeding
d-using electronic over-lode coated with epoxy(55c)
e- = analog gas-proof meter (A,V….)
f- = (0.6m3)valum for each stater starter.
g- = ( light+sockets+servic) cubicals.
h- = sump-pump starter =
I- = altra sonic level control system&all wiring.
j- = power factor improving units up to 90kvr*3
k- =service sockits 3*100A& 2*50A.
l- supply 25-no gas proof florcent fitings +5no 400w sodium
m- three spare cubicals
03-01-0064 | 5-geat valve with acuatures(800mm)(380v,50hz)with all acsseries. | 3
03-01-0065 | 6-non-return valves (800mm) with water hamer damper. | 3
03-01-0066 | 7-greas pumps work automaticly with all acsseries | 3
03-01-0067 | 8-using mimic control system (voltag,current,hz,levels,inducation lamps | 1
9-the supplier responsible on the phisical dimantions,taken from rustamya project
SECTION:1-1-10 :CABLES
code no. | description | qty
03-01-0068 | P.V.C cables 4-core flex, 1000v,double insulation 4*1.5mm2 | 4000m
03-01-0069 | = 4*2.5mm2 | 3000m
03-01-0070 | = 4*4 mm2 | 2000m
03-01-0071 | = 4*6 mm2 | 2000m
03-01-0072 | = 4*10mm2 | 2000m
03-01-0073 | = 4*16mm2 | 2000m
03-01-0074 | = 4*25mm2 | 1500m
03-01-0075 | = 4*50mm2 | 2000m
03-01-0076 | = 4*75mm2 | 2000m
03-01-0077 | = 4*125mm2 | 2000m
03-01-0078 | = 4*175mm2 | 2000m
03-01-0079 | = 4*240mm2 | 1000m
SECTION:1-1-11 :AIR CONDITION
code no. | description | qty
03-01-0080 | air-condition unit 24000 b.t.u. (cool-heat ) 3-speed fan 3-ph, with stenlessteel pips | 20
SECTION:1-1-12 : of different testers&elctrical - mechanical mat
code no. | description | qty
03-01-0081 | 1-A.V.O meter anloge (fluck) germany,0-2M ohm-0-10A-0-1000v | 10
03-01-0082 | 2- = = digital = =============== | 10
03-01-0083 | 3-clamp = anloge = 0----800A | 10
03-01-0084 | 4-Ohm- = = = 0---1ohm,0---10ohm,o---100ohm | 2
03-01-0085 | 5-set of wirnch germany up to 36mm | 5
03-01-0086 | 6- = = box spaner up to 36 mm | 10
7-end cables terminals (coper coated with anti-corasive )
03-01-0087 | 2.5mm2 | 2000
03-01-0088 | 4mm2 | 2000
03-01-0089 | 6mm2 | 2000
03-01-0090 | 10mm2 | 2000
03-01-0091 | 16mm2 | 2000
03-01-0092 | 25mm2 | 1500
03-01-0093 | 50mm2 | 1500
03-01-0094 | 75mm2 | 1500
03-01-0095 | 100mm2 | 1500
03-01-0096 | 125mm2 | 1500
03-01-0097 | 150mm2 | 1500
03-01-0098 | 175mm2 | 1500
03-01-0099 | 240mm2 | 1500
03-01-0100 | 8-electrical mager tester 0--------------5000v,up to 2000Mohm, hand charging | 5
03-01-0101 | 9-electrical welding mechine up to 500A ,220v,50hz,with mask&holder,carge type | 3
03-01-0102 | 10- = partible welding mechine 160A,220v,50hz,with mask&holder | 3
03-01-0103 | 11-tab wrench set up to 22mm | 5
03-01-0104 | 12-clamp - on vise up to 4 inch germany made | 10
03-01-0105 | 13-table vise = = 8 = = = | 3
03-01-0106 | 14-spot welding mechine 220v,50hz,up to 10mm,wetar coolent | 2
03-01-0107 | 15-drill-hamer germany made 220v 50hz 800w up to 13mm two speed &set of ponte | 3
03-01-0108 | 16- = ======================= 1500w, up to 22mm = = ======= | 3
03-01-0109 | 17- hydraulic jack (germeny made) 5 tone | 5
03-01-0110 | 18- =================== 10 = | 3
03-01-0111 | 19- universal swivel mechine vise (4--inch) with dgree reselution | 1
03-01-0112 | 20-table grinding mechime ,220v,50hz,two disc,three speed,700w, | 10
03-01-0113 | 21-hydraulic puller set up to 20 tone , ( 12 inch) | 5
03-01-0114 | 22- pull -- lift 2-tone ,with stenlessteel chane ,length of 15M | 9
03-01-0115 | 23- ==== 5-tone, ======================== 20M | 6
03-01-0116 | 24-========= 10-tone,======================= 25M | 6
SECTION: 1-1-13: screen for rustamya(orgenal phase)
code no | description | qty
03-01-0117 | 1-. Ames-crosta screen or equivlent as in fig(sc) the mash width of one set | 4
the new screen most be working on at less two metar highr then the old one
and the mash level .
2- the supplire most supply conver system to lift the screening out side of screen
house automatecly .
3-supply cran ,control penal,automatec control system (altra-sonic)
4- = all the metal equipment made from stenlssteel .
5- = = = the roller using in conver made from stenlssteel & polts
6- the supplier responsible on the phisecal dimantion to supply new screen with
2-M high from the old one.
SECTION:1-1-14: of gate-valvs -- non return valves
code no | description | qty
supply valves with the general note:
a-the spendel made from stanlessteel.
b-the fram = = cast iron with hand whell.
c-the sleve = = stanlessteel.with polt sets.
03-01-0118 | 1-pn-4 200mm length 225mm gate valve | 20
03-01-0119 | 2- = 150mm = 205mm gate valve | 10
03-01-0120 | 3- = 100mm = 185mm = = | 10
03-01-0121 | 4- = 100mm = 175mm = = | 10
03-01-0122 | 5- = 150mm = 210mm === | 10
03-01-0123 | 6- = 150mm = 260mm = = | 20
03-01-0124 | 7-pn16 150mm = 350mm non-return valve | 15
03-01-0125 | 8- = 400mm ========= | 5
03-01-0126 | 9- = 250mm = 600mm ========= | 10
03-01-0127 | 10- = 150mm = 395mm ========= | 10
03-01-0128 | 11- = 100mm ========= | 5
SECTION:1-1-15 : different material
code no | description | qty
03-01-0129 | 1-wade root blower or equivlint type sr091.7113 with motor 20kw 380v,dalta,1480rpm | 2
2-bearing :
03-01-0130 | 7216 | 20
03-01-0131 | 7219 | 20
03-01-0132 | 1320k | 20
03-01-0133 | 1317k | 20
03-01-0134 | 32221 | 20
03-01-0135 | 33122 | 20
03-01-0136 | 32234 | 20
03-01-0137 | 32236 | 20
03-01-0138 | 7224 | 20
03-01-0139 | 3-automatec greas pump with motor & control penal &5kg contaner | 10
03-01-0140 | 4-gas sensor divec with digital screen & sonic alarm to detect h2s gas in sewage | 10
plant with catloges
SECTION: 1-1-16: steel structurs&pumps
code no | description | qty
03-01-0141 | 1-detritor (scrapper&classifier) | 5
a-scrapper type dorr-oliver type w.a (fig 1-a)
b-classifier = = = = l w a - s (fig 1-b)
with gear box type : machin fabric a w g. bierens & zonen n.v/ holand
type w b v - 26 ,ratio 60-1 , 2.2 kw,with motor 750rpm
with control penal ( puls timer working )
03-01-0142 | 2-detritor (scrapper&classifier) | 2
scrapper type :dorr - oliver (fig 1-c) type"A" size (0-4)
deep collection tank (915dia*183deep)mm
cleaing chanal (1250long*69wide)mm
with control penal ( puls timer working )
03-01-0143 | 3-scrow pump with lower bearing and greas pump capacity 600 m 3/h | 3
rateau/france (fig 2 ).
03-01-0144 | 3-scrow pump with lower bearing and greas pump capacity 960m3/h,54.9rpm | 4
hubart sneek,length of screw with out breackets 9516mm,with lower 10569mm
length of winding 8586mm ,outer dia 1100mm,inner dia 660mm
03-01-0145 | 4- virtical pump q=350l/s h=15m 45kw 375rpm for activated sludge lifting | 4
with slip-ring motor 380v,50hz,375rpm,ip23,p.t.c.,with complet set of virtecal
shaft,greas pump,control penal with spesfication:
a-using bus-bar - cable-zoon,power factor units.
b-= AC3 for stater feeding 250A&electronic over lode
c- = three stage air-resistant rotor starting.
d- = MCCB for motor protaction
e- = altra-sonic level control system with wiring
f- = starters for sump-pump & lights& sockets& servic.
g- supply non-retun , gate-valves ,the supplier is responsible
on the phisical dimantions taken from rustamya project.
h-supply gas proof florcent fitings (20no&400w sodium)&wiring
SECTION: 1-1-17: of supply accessories to set of genrators
code no | description | qty
03-01-0146 | supply all the accessories systems for two bobinindus generators sets the | 1
gen. 2830kva,11kv ,m w m disel d- 6800 mannh eng. Type tbd 510-lo8
engen no 510.08.01033,2940kw,750rpm
a v k d6078 nev - isenburg type/didb 160618
11kv ,2830kva,the work inclode supply and the instulation to start the set in
sincronysing :
a-fule system
b-hydraulic =
c-coolent =
d-starting generator 175kva
e-control penal (HV,LV)with wiring.
f-change over switch(automatic)
g-labrecated system
h-all wiring,lighting,syncronysing system,stanlessteel radater
I-air starting system , with one year gearinty
SECTION :1-2 : karkh pumps sets
code no | description | qty
03-01-0147 | 1-virtecal pump q= 3000gpm,h=15.9m,965rpm,size350/350,55kw, | 4
03-01-0148 | 2-slip-ring motor 55kw,970rpm, | 2
03-01-0149 | 3-virtecal drive shaft set (3-pices)with all bracket | 2
03-01-0150 | 4-virtecal pump q=6000gpm,980rpm,110kw,h=14.9m,size350/400 | 2
03-01-0151 | 5-slip-ring motors 110kw,980rpm,380v | 2
03-01-0152 | 6-virtecal drive shaft set (3-pices)with all bracket | 2
03-01-0153 | 7-virtecal pump q=500gpm,1430rpm,h=21.1m,size150/200 | 30
03-01-0154 | 8-slip ring motor 30kw,1430rpm,v1 | 30
SECTION: 1-3 : REQUIREMENTS OF RUSTAMIYA TREATMENT PLANT , EXTENSION 3
SECTION :1-3-1: LOWER BERING
CODE NO | DESCRIPTION | QTY
03-01-0155 | lower bearing for screw pump | 12
type :OL180
Oil seal ring :BA 180x210x15(with s.s spring) .
SECTION : 1-3-2: WHEEL OF SETTLING TANK
CODE NO | DESCRIPTION | QTY
03-01-0156 | Type of solid rubber and vulkolln tires; | 500
(Cylindrical .st.and DG. tires)
diemension; vorwerk-445/335-75mm.
out dia;445mm.
inner dia;335mm.
thickness;75mm.
SECTION : 1-3-3: HIGH VOLTAGE CIRCUET BREAKER
CODE NO | DESCRIPTION | QTY
complete high voltage 11 kv circuet breaker,.
4 groups in 4 power stations, includes (ups) system,
chargers with batterey,s ,all protections,vacuum type
are request,motorized and mechanically charging,
deatails and drawings,all accessories, internal dies-
tribution bus-bars,spare parts for 3 years.
Group 1
03-01-0157 | Incoming feeder c.b | 2
Voltage; 12kv
Currrent;1250A
Short time current 3 sec/ 25KA
Making current 70 KA
03-01-0158 | Bus section c.b | 1
Voltage; 12kv
Currrent;1250A
Short time current 3 sec/ 25KA
Making current 70 KA
03-01-0159 | Measuring section cubature with fuses set. | 1
03-01-0160 | Cable feeder c.b | 3
Voltage; 12kv
Currrent;800A
Short time current 3 sec/ 25KA
Making current 70 KA
03-01-0161 | Transformer feeder c.b | 5
Voltage; 12kv
Current;800A
Short time current 3 sec/ 25KA
Making current 70 KA
GROUP 2 and 3 are resembly
03-01-0162 | Incoming feeder c.b | 4
Voltage; 12kv
Current;800A
Short time current 3 sec/ 25KA
Making current 70 KA
03-01-0163 | Measuring section cubature with fuses set. | 2
03-01-0164 | Transformer feeder c.b | 8
Voltage; 12kv
Currrent;800A
Short time current 3 sec/ 25KA
Making current 70 KA
GROUP 4
03-01-0165 | Incoming feeder c.b | 2
Voltage; 12kv
Current;800A
Short time current 3 sec/ 25KA
Making current 70 KA
03-01-0166 | Measuring section cubature with fuses set. | 1
03-01-0167 | Transformer feeder c.b | 3
Voltage; 12kv
Current;800A
Short time current 3 sec/ 25KA
Making current 70 KA
SECTION: 1-3-4: MOTORS
CODE NO | DESCRIPTION | QTY
ALL MOTORS MUST BE INDUCTION TYPE/ AEG,
OR EQUIVALENT.
03-01-0168 | Type; AM 315 MQ4 (B3) | 10
Power;200 KW
Speed; 1485 rpm.
Voltage; 400 v delta/ 50 HZ
Protection;IP54
03-01-0169 | Type; AM 160 LR4 (B3) | 15
Power;15 KW
Speed; 1460 rpm.
Voltage; 400 v delta/ 50 HZ
Protection;IP54
03-01-0170 | Type; (B3). | 10
Power; 18.5 KW
Speed; 1460 rpm.
Voltage; 400 v delta/ 50 HZ
SECTION: 1-3-5: POWER FACTOR CORRECTION UNITS,
CODE NO | DESCRIPTION | QTY
03-01-0171 | EACH UNIT HAS A FOLLOWING:--- | 4
Dry type are request.
KVAR = 3 x 600
HZ = 50
Voltage = 3 x 400 v
Ampper = 3 x 866
Man. and Auto.
SECTION 2 : WATER TREATMENTS PLANT AND NETWORKS REQUIREMENTS
SECTION 2-1: SPARE PARTS FOR KARKH RESERVOIRS
ABU GHRAIB RES. REQUIREMENTS
CODE NO. | DESCRIPTION | QTY
SPARES FOR 400/400/410 D.E.SC. PUMP WORKING NO. C5/56450/51 DROWING NO. P.2003142
03-01-0172 | COMPLET ROTATING ELEMENT | 2
03-01-0173 | INDUCTION MOTOR | 2
03-01-0174 | IMPELLER | 1
03-01-0175 | CASING EYE RING | 2 set
03-01-0176 | IMPELLER EYE RING | 2 set
03-01-0177 | THRUST WASHER | 6
03-01-0178 | BEARING HOUSING | 1
03-01-0179 | LANTERN RING (IN HALVES) | 2
03-01-01710 | SPACER RING | 2
03-01-01711 | ROLLER THRUST BEARING | 5
03-01-01712 | MOTOR HALF COUPLING | 5
03-01-01713 | PUMP HALF COUPLING | 5
03-01-01714 | SHAFT SELVES | 3
03-01-01715 | PRESSURE SWITCH TYPE 107 | 7
03-01-01716 | DIFFERENTIAL PRESSURE SWITCH TYPE 217 | 7
03-01-01717 | 500mm BUTTER FLY VALVE WITH ELECTRIC ACTUATOR NEWTON CHAMBER LIMITORQ | 2
03-01-01718 | ACTUATOR WITH GEAR LIMITOR FOR 500mm VALVES | 5
03-01-01719 | BALL BEARING SKF 6318 | 10
03-01-01720 | 800mm BUTTER FLY VALVES WITH ELECTRIC ACTUATOR NEWTON CHAMBER LIMITORQ | 1
03-01-01721 | ACTUATOR WITH GEAR LIMITOR FOR 800mm BUTTER FLY VALVES | 4
03-01-01722 | GLAND PACKING | 3set
03-01-01723 | COMPLETE DRIVE SHAFTING | 2
SPARES FOR 350/300/429 D.E.SC. PUMP WORKING NO. C5/56454 DROWING NO. P.2003140 (AUB GHRAIB RES.)
03-01-01724 | ROTATING ELEMENT | 2
03-01-01725 | INDUCTION MOTOR | 1
03-01-01726 | IMPELER | 2
03-01-01727 | CASING EYERING | 1set
03-01-01728 | IMPELER EYE RING | 1set
03-01-01729 | LANTERN RING (IN HALVES) | 2
03-01-01730 | SPACER RING | 4
03-01-01731 | ROLLER THRUST BEARING | 4
03-01-01732 | BOTTOM BEARING BUSH | 2
03-01-01733 | MOTOR HALF COUPLING | 2
03-01-01734 | PUMP HALF COUPLING | 2
03-01-01735 | PLUMMER BLOCK ITEM (22 , 23 , 24) | 2
03-01-01736 | THRUST WASHER | 6
03-01-01737 | PRESSURE SWITCH TYPE 107 | 2
03-01-01738 | DIFFERENTIAL PRESSURE SWITCH TYPE 217 | 2
03-01-01739 | 400mm BUTTER FLY VALVES WITH ELECTRIC ACTUATOR NEWTON CHAMBER LIMITORQ | 2
03-01-01740 | ACTUATOR WITH GEAR LIMITOR FOR 400mm VALVE | 2
03-01-01741 | ANGUALAR CONTACT BEARING SKF 7318B | 10
03-01-01742 | BALL BEARING SKF 6315 | 6
03-01-01743 | THRUST BEARING NTN 51205 | 20
03-01-01744 | GLAND BACKING | 4set
03-01-01745 | COMPLET DRIVE SHAFTING | 1
CODE | DESCRIPTION | QTY
03-01-01746 | DRAINAGE PUMP HEAD 10m , POWER 0.75 Kw OUT PUT PIPE 1" | 4
03-01-01747 | BASEMENT FLOODED ALARM PANEL , SERIAL NO. C1880/47 FO2 , INCOMING SUPPLY 230 V , CONTROL SUPPLY 110V , MODULAR CONTROL L.T.D | 1
03-01-01748 | COMPLETE GENERATOR NEATRAL EAR THING , N.E.L REYROLLE BELMOS , SUPLY 400V , 50Hz , BUSBAR RATING 1000A REFERENC NO. 13/543/27 | 1
03-01-01749 | ERTHING RELAY , D-2600 , 90A A.C , 600V , 60Hz , 3PH , COIL VOLTAGE 110V , 50 Hz , VOLTAGE = 220 , 440 , 600 , POWER(hp) = 32 , 64 , 78 , COMPLETE WITH AS 1029 , RATING FOR IEC , SK415021 - G | 8
CODE | DESCRIPTION | QTY
CONTACTOR ASEA :
03-01-01750 | EG 315-1 , IEC 158-1 , Ith 355A | 3
03-01-01751 | EG 80-1 , Ith 110A | 10
03-01-01752 | EG 630-2 , IEC 158-1 , Ith 630A | 10
03-01-01753 | EG 10 , SK 412 , 0112 , Ith 16A | 10
ELECTRONIC TIMER :
03-01-01754 | TYPE : D 0/5M-05 , RANGE : 0-1 MIN , VOLT = 110 V A.C , 8-PINS | 10
03-01-01755 | TYPE : D 0/5M-02 , RANGE : 0-3 MIN , VOLT = 110 V A.C , 8-PINS , MANUFACTURES = CHROMALOCK LIMITED | 10
CODE | DESCRIPTION | QTY
03-01-01756 | PUMP STATION 400/400/410 D.E.SC. PUMP , SERIAL NO. C5/56450/51 DROWING NO. P.2003142 | 3
1- COMPLETE PUMP WITH MOTOR AND SHAFT INCLUDING .
2- MOTOR COOLER PIPE WORK & PRESSURE SWITCHES .
3- MANUAL VALVES WITH HANDLE .
4- ELECTRIC VALVES WITH HANDLE .
5- ELECTRIC CONTROL BOARD WITH INSTRUMENT AND CABLES .
6- MANUAL VALVE (FOR MAINTEN ANCE)
7- PIPE & VIKING JOHRSON AND ALL CONNECTION AND ADAPTORS.
8- REFLUX VALVES / NON RETURN VALVES
9- ACTUATORS
10- POWER FACTOR CORRE CTION CAPACITOR
NORTH & SOUTH RES
CODE | DESCRIPTION | QTY
SPARE PARTS FOR ALLEN DESIEL TYPE 16V+B196 512 FX-B
GENERATING STATION
03-01-01757 | TACHO WITH SPRING DRIVE PART NO. KS 22407 | 4
03-01-01758 | GOVERNOR JOINT PART NO. KS 24237 | 4
03-01-01759 | INLET VALVE PART NO. SD 52533 | 32
03-01-01760 | EXHAUST VALVE CSTELLITE SEAT PART NO. SD 52534 | 32
03-01-01761 | OUTER VALVE SPRING PART NO. SD 88383 | 64
03-01-01762 | INLET VALVE GUIDE PART NO. SD 86044 | 32
03-01-01763 | EXHAUST VALVE GUIDI PART NO. SD 86045 | 32
03-01-01764 | FUEL OIL FILTER PART NO. SD 55583 | 40
03-01-01765 | ELEMENT PART NO. SD 89576 | 12
03-01-01766 | LUBRICANT OIL FILTER PART NO. SD 54685 | 64
03-01-01767 | JOINT WASHER FOR INJECTOR PART NO. SD 17985 | 16
03-01-01768 | FUEL INJECTOR NOZZLE PART NO. S 94307 | 64
03-01-01769 | NOZZLE HOLDER ASSEMBLY PART NO. SD 95077 | 32
03-01-01770 | WASHER PART NO. KS 17262 | 32
03-01-01771 | WASHER - INLET CONNECTOR PART NO. SD 48595 | 32
03-01-01772 | GUIDED SPINDLE PART NO. D 52057 | 32
03-01-01773 | GUIDED THRUST SPINDLE PART NO. D 52058 | 32
03-01-01774 | NOZZLE HOLDER BODY PART NO. SD 094320 | 32
03-01-01775 | FUEL INJECTION PUMP ASSEMBLY PART NO. SD 95078 | 32
03-01-01776 | PLUNGER SPRING PART NO. SD 46774 | 16
03-01-01777 | SPRING WASHER PART NO. SD 46778 | 16
03-01-01778 | WASHER FOR BINKING PLUG PART NO. SD 46780 | 16
03-01-01779 | AIR VENT SCREW WASHER PART NO. SD 88857 | 16
03-01-01780 | DELIVERY VALVE AND SEAT ASSEMBLY PART NO. SD 94495 | 16
03-01-01781 | LOW PRESSURE SEAL (VITON) PART NO. D 94353 | 16
03-01-01782 | DELIVERY VALVE HOLDER (DISCHARGE UNION) PART NO. SD 94251 | 4
03-01-01783 | JOINT FOR GLACIER FILTER (GLACIER) G.F.2 FILTER PART NO. SD 94252 | 4
03-01-01784 | 25 NB VALVE PART NO. SD 94477 | 4
03-01-01785 | (AMOT) TYPE 414 OF PRESSURE SWITCH PART NO. D 1005065 | 4
03-01-01786 | (AMOT) STARTING AIR PESSURE SWITCH PART NO. D 1005068 | 2
03-01-01787 | 1-1/2" 3WAY VALVE T-PORT PART NO. D 1007464/330 | 2
03-01-01788 | T.A.V FLOAT SWITCH TYPE 70/270 PART NO. D1007464/369 | 2
03-01-01789 | WOOD WARD BOOSTER SERVO - MOTOR PART NO. D 1007464/393 | 2
03-01-01790 | 6KW IMMERSION HEATER PART NO. D 1007464/454 | 2
03-01-01791 | THERMOSTAT FOR IMMERSION HEATER PART NO. D 1007464/455 | 2
03-01-01792 | TEMPERATURE SENSOR PART NO. D1007464/677 | 12
03-01-01793 | 40 NB GATE VALVE PART NO. SD 94457 | 4
03-01-01794 | (AMOT)THERMOSTATIC TEMPERATURE CONTROL VALVE PARTNO.SD94692 | 2
03-01-01795 | PYROPRESS SOLENOID AIR VALVE BORE PART NO. D 1007464/607 | 4
03-01-01796 | JOINT FOR EXHAUST PIPE FLANGE PART NO. SD 58907 | 36
03-01-01797 | JOINT FOR PULSE CONVERTER OUTLET PART NO. SD 59386 | 4
03-01-01798 | JOINT FOR EXHAUST BEND INLET TO TURBO CHARGER PART NO. SD59387 | 8
03-01-01799 | JOINT FOR CYLINDER HEAD FLANGE PART NO. SD 4323 | 16
03-01-01800 | JOINT FOR COVER PLATE PART NO. SD 49698 | 2
03-01-01801 | JOINT FOR AIR MANIFOLD PLATE PART NO. SD 51158 | 1
03-01-01802 | JOINT FOR BLOWER EXHAUST OUTLET PLATE PART NO. SD 88280 | 4
03-01-01803 | JOINT FOR CHARGE AIR COOLER PART NO. SD 87322 | 2
03-01-01804 | JOINT FOR CHARGE AIR COOLER OUTLET BAND PART NO. SD 87324 | 4
03-01-01805 | 2-1/2" PRESSURE GAUGE (0-7)bar PART NO. SD 87568 | 8
03-01-01806 | 2-1/2" PRESSURE GAUGE (0-4)bar PART NO. SD 87571 | 2
03-01-01807 | JOINT FOR AIR INLET BENDMANIFOLLD END PART NO. SD 48331 | 2
03-01-01808 | AIR RECEIVER ANCONTROL VALVES CPMPLET | 4
03-01-01809 | WATER PUMPE DRIVE BEARING PART NO. SD 86055 | 2
CODE | DESCRIPTION | QTY
PORTCELL EQUIPMENTS
ANGLE VALVE
03-01-01810 | TYPE VA23 12mm BSP , CLORINE DRAM CONNECTION HAND WHEEL | 15
03-01-01811 | TYPE VC35-25mm , HEADER ISOLOTION | 10
03-01-01812 | PLUG VALVE - 2WAY
03-01-01813 | TYPE 067-25mm , ELETRIC ACTVOTER WITH MANUAL OVER RID SUPPLY 110V , 1ph , 50Hz | 5
03-01-01814 | TYPE 062 - 25mm , LEVER WITH LOCKING DEVICE | 8
03-01-01815 | TYPE 066 - 12 mm , LEVER WITH LOCKING DEVICE | 13
03-01-01816 | NON - RETURN VALVE , TYPE : A2/4821 ,25mm , 1 1/2" BSP , FOR LIQEEL CLOMETER | 10
CLORINATOR
03-01-01817 | TYPE :31AE , 27Kg/hr MAX MANUAL SET DOSE WITH OUTOMATIC PROPERTIONING TO FLOW | 2
03-01-01818 | TYPE :21AE , 14Kg/hr MAX MANUAL SET DOSE WITH OUTOMATIC PROPERTIONING TO FLOW | 6
03-01-01819 | AUTOMATIC CHLORINE DRUM CHANGE OVER PANEL : FOR FIVE DRUM SEQUENCE CONTROL | 1
03-01-01820 | ANALYSER TYPE : SERISE 66 , RESIDUL ANALYSER PORTACAL CO. | 10
03-01-01821 | CHLORINE LEAK DETECTORS | 5
BBC. KENT INDUSTRIAL MESUREMENTS
CODE | DESCRIPTION | QTY
03-01-01822 | ELECTRANIC TRANSMITTER | 4
1- VERSION : STANDARD WITH BADY BOLTS AND NUTS IN HIGH TENSILE CARBON STEEL .
2- BODY : CARBON STEEL
3- MEASURING ELEMENT 0.1 - A151 316 SILICONE OIL CAPSUULE IN SPAN 500 TO 5200 (20-205)
4- SEALS PTFE SILICONE RUBBER
OUT PUT 4-20 Ma
FOR / LEVEL :
03-01-01823 | SPARE / ELECTRONIC UNIT | 6
03-01-01824 | CAPILLARY TUBE 1/2" OD | 20
03-01-01825 | NYLON TYPE 30m REEL 1/8" | 15
03-01-01826 | BRASS COVPLING TO SUIT 1/8" | 500
03-01-01827 | BRASS FERRULE | 200
600/600/600 D.E.S.C PUMP SECTION DROWING NO. P2003177 SER.NO. C5/56429/30
CODE | DESCRIPTION | QTY
03-01-01828 | ROTATING ELEMENT | 6
03-01-01829 | INDUCTION MOTOR | 2
03-01-01830 | CASING SPACER RING ST | 6
03-01-01831 | GLAND PACKING ST | 3
03-01-01832 | 800mm BATTER FLY NEWTON CHAMBER VALVES WITH ELECTRIC LIMITORG ACTUATER | 4
03-01-01833 | ACTUATER WITH GEAR LIMITION | 20
03-01-01834 | 900mm BATTER FLY NEWTON CHAMBER VALVES WITH ELECTRIC LIMITORG B289ACTUATER | 4
03-01-01835 | 500mm BATTER FLY NEWTON CHAMBER VALVES WITH ELECTRIC LIMITORG ACTUATER | 4
03-01-01836 | WORM SHAFT H020-05-1L | 10
03-01-01837 | WORM SHAFT H018-06-1L | 20
03-01-01838 | THRUST BEARING NTN 5/205 | 40
03-01-01839 | THRUST BEARING NTN 5/306 | 40
03-01-01840 | TAPER PIN 6x60mm | 20
03-01-01841 | SOCKET SET SCR M12x16mm | 20
03-01-01842 | BEARING BUSH 35x45x15 | 20
03-01-01843 | BEARING BUSH 25x35x25 | 20
03-01-01844 | DRIVE SHAFTING | 1
03-01-01845 | COMPLETE PUMP WITH MOTOR AND SHAFT INCLUDING :- | 3
1- NON RETURN VALVES/REFLUX VALVES
2- MANUAL VALVES WIT HANDLE
3- ELECTRIC VALVE WITH HANDLE
4- ELECTRIC CONTROL BOARD WITH INSTRUMENT
5- MANUAL VALVES (FOR MAINTENCE)
6- PIPES & VIKING JOHNSON AND ALL NECESSARY CONNECTIONS & ADAPTORS
7- MOTOR COOLER PIPE & PRESSURE SWITCHES
CODE | DESCRIPTION | QTY
PORTECEL CHLORINATOR B701PUMPS
03-01-01846 | PUMP R 32 - 250 CHEMICAL , FUGEL PUMP : DUTY 1.389 L/S , H : 76m , 2950 rpm , MOTOR 8.1 KW , 400V , 3ph , 50 Hz | 3
03-01-01847 | PUMP R 32 - 250 CHEMICAL CENTER FUGEL PUMPS : DUTY 2.5 L/S , H :91m , 2950 rpm , MOTOR 12.6 KW , 400V , 3ph , 50 Hz | 1
03-01-01848 | PUMP R 32 - 250 CHEMICAL CENTER FUGEL PUMPS : DUTY 1.389 L/S , H :87m , 2950 rpm , MOTOR 12.1 KW , 400V , 3ph , 50 Hz | 1
03-01-01849 | COMPLETE ROTATING ELEMENT FOR THE PUMP | 6
03-01-01850 | COMPLETE ROTATING ELEMENT FOR THE MOTOR | 2
03-01-01851 | STATAR MOTOR 8.1 KW | 4
03-01-01852 | STATAR MOTOR 12.6 KW | 2
03-01-01853 | STATAR MOTOR 12.1 KW | 1
03-01-01854 | SET OF GLAND PACKING | 20seT
03-01-01855 | BOLL BEARING | 20
03-01-01856 | BEARING NO. 6207 | 10
03-01-01857 | BEARING NO. 6310 | 10
03-01-01858 | OILER FILLING | 2
FUSE & BULB
CODE | DESCRIPTION | QTY
03-01-01859 | BULB 12V (SCREW CAP ETO) | 200
03-01-01860 | MAIN FUSE TBC10 | 500
03-01-01861 | MAIN FUSE TBC16 | 500
03-01-01862 | MAIN FUSE TBC20 | 500
03-01-01863 | MAIN FUSE TBC25 | 500
03-01-01864 | MAIN FUSE TBC32 | 500
03-01-01865 | MAIN FUSE TBC40 | 500
03-01-01866 | MAIN FUSE TBC50 | 200
03-01-01867 | MAIN FUSE TBC63 | 200
03-01-01868 | MAIN FUSE TC100 | 200
03-01-01869 | MAIN FUSE TF125 | 200
03-01-01870 | MAIN FUSE TF160 | 200
03-01-01871 | MAIN FUSE TF200 | 200
03-01-01872 | MAIN FUSE TIA4 | 200
03-01-01873 | MAIN FUSE TIA6 | 200
03-01-01874 | MAIN FUSE TIA10 | 500
03-01-01875 | MAIN FUSE TIA20 | 500
03-01-01876 | MAIN FUSE TIA25 | 500
03-01-01877 | MAIN FUSE TIA32M40 | 500
03-01-01878 | MAIN FUSE TIS35 | 500
03-01-01879 | MAIN FUSE TIS63M80 | 500
03-01-01880 | MAIN FUSE TM355 | 500
03-01-01881 | MAIN FUSE TM400 | 500
03-01-01882 | MAIN FUSE TKF250 | 500
03-01-01883 | MAIN FUSE TKF315 | 100
03-01-01884 | MAIN FUSE TKF355 | 100
03-01-01885 | MAIN FUSE TTM636 | 100
03-01-01886 | CONTROL FUSE NIT4A | 500
03-01-01887 | CONTROL FUSE NIT6A | 500
03-01-01888 | CONTROL FUSE NIT26A | 500
03-01-01889 | RESISTOR - 100K (PKT OF 10) | 3
03-01-01890 | RESISTOR - 11K (PKT OF 10) | 3
03-01-01891 | RESISTOR - 150 ohm (PKT OF 10) | 3
03-01-01892 | RESISTOR - 120K (PKT OF 10) | 3
03-01-01893 | RESISTOR - 150K (PKT OF 10) | 3
03-01-01894 | RESISTOR - 200 ohm (PKT OF 10) | 3
03-01-01895 | RESISTOR - 6.2K (PKT OF 10) | 3
03-01-01896 | RESISTOR - 51K (PKT OF 10) | 3
03-01-01897 | RESISTOR - 33K (PKT OF 10) | 3
03-01-01898 | RESISTOR - 1M (PKT OF 10) | 3
03-01-01899 | RESISTOR - 15K (PKT OF 10) | 3
03-01-01900 | QUAD Op-Amps | 10
03-01-01901 | TRANSISTOR 12VA | 15
03-01-01902 | REGULATOR , 12V | 6
03-01-01903 | RELAY 24V D.C | 6
03-01-01904 | TIMER , TYPE 2240 | 6
03-01-01905 | 556 TIMER | 6
03-01-01906 | TRANSISTOR | 15
SECTION 2-2: DESINFECTION SYSTEM
CODE | DESCRIPTION | QTY
03-01-01907 | CHLORINATOR WITH CAPACITY 1000g/h CONSISTS THE FOLLOWING | 20
1- WALL MOUNTED CONTROL UNIT
2- INJECTOR
3- VACCUM AND PRESSURE CONTROL UNITS
4- MANUUAL CONTROL SWITCHOVER VALVE
5- FLEXIBLE CONNECTIONS BETWEEN THE UNITS
6- ALL THE VALVES AND FITTINGS
7- LEAD WASHER 1000 PEC. FOR EACH .
8- SPARE PARTS FOR ALL A/ M ITEMS
THE PREFERABLE TYPES WALLACE&TIRNANE AND THE CAPETAL ONTRO
03-01-01908 | THE SYSTEM INCLUDES THE FOLLOWING : | 20
1- CHLORINATORS :
CAPACITY OF EACH ONE 2 Kg /h CONSISTING ALL THE CONNECTING PIPES AND FITTINGS , INJECTORS ,MANOMETERS FOR THE GAS AND THE WATER .
2- a- FLEXIBLE PIPES AND VALVES SUPPLIED TO BE CONNECTED BETWEEN THE CHLORINEATORS AND THE GAS CYLINDERS .
b- FLEXIBLE HOSE (REINFORCED HOSE) SIZE 1.5" OR 2" WITH ALL THE FITTING TO BE COUNECTED BETWEEN THE INJECTORS AND THE INJECTION POINT (LENGTH 25 m) .
C- ITEMIZED SPARE PARTS FOR ALL THE EQUIPMENTS MOUNTED INSIDE THE CONTAINER .
03-01-0909 | 1- CHLORINATORS | 20
CAPACITY OF EACH ONE 5 Kg /h CONSISTING ALL THE CONNECTING PIPES AND FITTINGS , INJECTORS ,MANOMETERS FOR THE GAS AND THE WATER .
2-a- FLEXIBLE PIPES AND VALVES SUPPLIED TO BE CONNECTED BETWEEN THE CHLORINEATORS AND THE GAS CYLINDERS .
b- FLEXIBLE HOSE (REINFORCED HOSE) SIZE 1.5" OR 2" WITH ALL THE FITTING TO BE COUNECTED BETWEEN THE INJECTORS AND THE INJECTION POINT (LENGTH 25 m) .
C- ITEMIZED SPARE PARTS FOR ALL THE EQUIPMENTS
03-01-0910 | THE SYSTEM INCLUDES THE FOLLOWING : | 30
1- CHLORINATORS
CAPACITY OF EACH ONE 10 Kg /h CONSISTING ALL THE CONNECTING PIPES AND FITTINGS , INJECTORS ,MANOMETERS FOR THE GAS AND THE WATER .
2- a- FLEXIBLE PIPES AND VALVES SUPPLIED TO BE CONNECTED BETWEEN THE CHLORINEATORS AND THE GAS CYLINDERS .
b- FLEXIBLE HOSE (REINFORCED HOSE) SIZE 1.5" OR 2" WITH ALL THE FITTING TO BE COUNECTED BETWEEN THE INJECTORS AND THE INJECTION POINT (LENGTH 25 m) .
C- ITEMIZED SPARE PARTS FOR ALL THE EQUIPMENTS .
03-01-0911 | 1- CHLORINATORS | 20
CAPACITY OF EACH ONE 20 Kg /h CONSISTING ALL THE CONNECTING PIPES AND FITTINGS , INJECTORS ,MANOMETERS FOR THE GAS AND THE WATER .
2- a- FLEXIBLE PIPES AND VALVES SUPPLIED TO BE CONNECTED BETWEEN THE CHLORINEATORS AND THE GAS CYLINDERS .
b- FLEXIBLE HOSE (REINFORCED HOSE) SIZE 1.5" OR 2" WITH ALL THE FITTING TO BE COUNECTED BETWEEN THE INJECTORS AND THE INJECTION POINT (LENGTH 25 m) .
C- ITEMIZED SPARE PARTS FOR ALL THE EQUIPMENTS .
SECTION 2-3: SPARE PARTS LIST FOR DEISEL ENGINE
DAIHATSU DIESEL MFG. CO, LTD.
OSAKA , JAPAN
ENGINE MODEL (8DV-26) ENG. SPEED 750 rpm
ENG NO. D826024V BORE 260 mm STROKE 320mm
CODE | DESCRIPTION | QTY
03-01-0912 | CRANK SHAFT ASSEMBLY FIG NO.9 | 1set
03-01-0913 | CAM SHAFT ASSEMBLY FIG NO. 11 | 1set
03-01-0914 | PISTON & CONNECTING ROD ASSEMBLY FIG NO. 24 | 16set
03-01-0915 | CYLINDER HEAD ASSEMBLY FIG NO. 25 | 16set
03-01-0916 | VALVE OPERATING DEVICE FIG NO. 28 | 16set
03-01-0917 | EXHAUST VALVE ASSEMBLY FIG NO. 27 | 16set
03-01-0918 | INTAKE VALVE ASSEMBLY FIG NO. 26 | 16set
SECTION 2-4: SPAR PART FOR CHLORINE GAS SYSTEM FROM FISCHER &
PORTER TO KARAMAH B676
CODE | DESCRIPTION | QTY
03-01-0919 | SET CONTAINER ROLLER TRUNNIONS CAPACITY FOR CONTAINER | 16
UP TO 1000 Kg .
03-01-0920 | ANCHOR BOLT M16 x 160 Mu , DIN 529 . | 96
03-01-0921 | WASHER 17 , DIN 125 . | 96
03-01-0922 | MANIFOLD 1" WITH 2 CONNECTIONS 1" DIN 11 , LENGTH 1000mm | 4
SER. NO. 628 A 1089
03-01-0923 | MANIFOLD 1" WITH 1 CONNECTIONS 1" DIN 11 , LENGTH 1000mm | 4
SER. NO. 628 A 1090
03-01-0924 | AUX. VALVE 1" - 1" DIN 11 , SER. NO. 125 A 1053 . | 24
03-01-0925 | SISC 1" , SER. NO. 374 B 1022 . | 4
03-01-0926 | GASKET 18/11mm , SER. NO. 377 N 1001 . | 200
03-01-0927 | BALL VALVE DN 25 FOR WELDING , SER. NO. 125A 1091 | 4
03-01-0928 | COPPER CONNECTOR 1.0 m , SER. NO. 628 A 1008 . | 16
03-01-0929 | AUTOM GAS CHANGE OVER PANEL MEDIUM : CHLORIN , | 2
CAPACITY : 60 Kg CL2/h , CONNECTION : 1" DIN 11, SER. NO.806A1032 .
03-01-0930 | CONTACT PRESSURE GANGE WITH CONNECTOR , RANGE : 0 - 10 bar | 2
PART NO. 131 C 1019 , SER. NO. ANL 1000 L04 , ANL 1000 KO1
03-01-0931 | CHLORINE FILTER WITH FLANGES , DN 25 WITH GROOVE AND | 2
TONGUE acc. DIN 2512 , SER. NO. 666A1031
FLANGE PAIR FOR WELDING DN 25 , DIN 2635 WITH GROOVE AND
03-01-0932 | TONGUE acc. DIN 2512 WITH SCREWS , HEX NUTS AND GASKETS , | 2
SER. NO. 614 L 1166
03-01-0933 | HEATER 220 V , 50 Hz , 48 w , SER. NO. 677 N 1042 . | 2
03-01-0934 | CHLORINE GAS REGULATOR , CAPACITY : max. 200 Kg CL2/h FOR | 6
WALL MOUNTING WITH GAS PRESSURE GANGE ,SER. NO. 806D190U06
03-01-0935 | CONTACT PRESSURE GANGE WITH CONSISTING OF EACH | 4
1 CONTACT PRESSURE GANGE 0 - 10 bar
1 WALL MOUNTING BRACKET
1 COPPER CONNECTOR , SER. NO. 630 B 1006 .
03-01-0936 | STEEL PIPE 1" , 33.7 x 2.6 mm , DIN 2448 . | 24 m
03-01-0937 | WELDING ELBOW 90 , 1" , 33.7 x 2.6 mm , DIN 2605 | 6
03-01-0938 | ANGLE SEAT VALVE DN 25 , PVC , PTFE , SER. NO. 161 . 300 . 449 | 12
03-01-0939 | CHLORINE GAS DISPENSER: | 16
MODEL N 70 C 4400 , TYPE 70 C 4494 ABXX IX2X UXCKD WITHOUT
VACUUM REGULATOR CAPPCITY:max.20 Kg CL2/h WITH INTEGRATED
CHLOROMATIC VALVE OPERATED FROM SINGAL OF WATER FLOW
POWER SUPPLIY : 220 V , 50 Hz , INPUT SIGNAL : 4 - 20 m A
METERING RANGE : 1- 20 Kg B64 WITH EJECTOR 806 E 063 U 06 FOR
WATER PRESSURE 4.6 bar , BACK PRESSARE 2 bar , WATER FLOW
2.96 L/S , CA. 10.7 m3/h , WIRING DIAGRAM acc. ANL 1000 E 07 .
03-01-0940 | STRAINER DN 80 , PVC , EPDM WITH SCREEM , ORIFICE 2.2 mm , | 2
SER. NO. 161 . 305 . 650
03-01-0941 | BALL VALVE DN 80 , PVC , EPDM , WITH FLANGES , SER. NO. 161.370.013 | 2
03-01-0942 | ANGLE SEAT VALVE DN 25 , PVC , PE , SER. NO. 161 . 300 . 550 | 12
03-01-0943 | ANGLE CHECK VALVE DN 80 , PVC , EPDM , SER. NO. 161 . 303 . 013 | 2
03-01-0944 | FLANGE ADOPTOR DN 80 , PVC , SER. NO. 721 . 700 . 013 | 12
03-01-0945 | FLANGE DN 80 , PVC SER. NO. 721 . 700 . 013 | 12
03-01-0946 | FLAT GASKET DN 80 , CR , SER. NO. 748 . 400 . 022 | 12
03-01-0947 | UNION DN 50 , PVC SER. NO. 721 . 510 . 110 . | 24
03-01-0948 | ANGLE SEAT VALVE DN50 , PVC , PTFE , SER. NO. 161 . 300 . 599 . | 12
03-01-0949 | BALL CHECK VALVE DN 50 , PVC , FPM , SER. NO. 161 . 360 . 036 . | 6
03-01-0950 | UNION DN 50 , PVC , RITON , SER. NO. 721 . 510 . 110 . | 6
03-01-0951 | SOLUTION WATER DIFFUSOR DN 50 , PVC , WITH ANGLE SEAT VALVE | 6
SER. NO. 806F1023
03-01-0952 | RESIDUAL CHLORINE ANALGZER , CHLORTROL 2" , MODEL D17 K2121CA | 2
CONSISTING OF : PRIMARY UNIT , SECUNDARY UNIT AND
CONNECTION CABLE , POWER SUPPLY : 220 V , 50 Hz, OUTPUT
SIGNAL : 4 - 20 m A , METERING RANGE : 0 - 2 mg CL2/L+B630
03-01-0953 | CONNECTION ACCESSORIES WITH PRESSURE READUONG VALVE | 2
SER. NO. 614 L 1422
03-01-0954 | SAMPLE LINE COMPLETE FOR LINE > DN 300 , SER. NO.614 L 1153 | 2
03-01-0955 | CHLORINE COMPARATOR LOVIBOND 1000 METERING RANGE : | 10
0.1 - 5 mg CL2/h , SER. NO. 142B1021
03-01-0956 | BREATHING PROTECTION MASK WITH FILTER B IN CARRYING BOX | 20
SER. NO.NOVA R A
03-01-0957 | CHLORINE LEAK DETECTOR , MODEL "CHLORALERT" , POWER | 2
SUPPLY : 220 V , 50 Hz , SER. NO. 17 CA1020
03-01-0958 | SET ACCESSORIES , SER. NO. 614 L 1192 | 2
03-01-0959 | SET SPARE PARTS , SER. NO. 614 L 1193 | 2
03-01-0960 | ALARM HORN 220V , 50 Hz , SER. NO. 151E1001 | 2
03-01-0961 | ALARM RESET COMBINATION , SER. NO. 151 E 1002 | 2
03-01-0962 | TEC DN 20 , PVC , SER. NO. 112 A 1049 | 2
03-01-0963 | PVC - CEMENT 500 cm3 , SER. NO. 141 B 1043 | 2
03-01-0964 | TANK LIFTING BEAM FOR CHLORINE CONTAINER VOLUME | 2
800 L = 1000 Kg CL 2 , SER. NO. 623 A 1058
03-01-0965 | SPRAY NOZZLE DN 15 , PVC , SER. NO. 130 F 1002 | 20
03-01-0966 | PVC - PIPE 32 x 1.8 , DN 25 , DIN 8061/62 | 60m
03-01-0967 | SHUT - OFF VALVE R 1" WITH LONGER SPINDLE,SER.NO.668A1063 | 4
03-01-0968 | ELBOW DN 25 , PVC , SER. NO. 721.100.108 | 20
03-01-0969 | SOCKET DN 25 , PVC , SER. NO. 721.910.108 | 12
03-01-0970 | TEC , REDUCING DN 25 - 15 - 25 , PVC , SER. NO. 721.200.141 | 16
03-01-0971 | REDUCING BUSH DN 25-15 , PVC , SER. NO. 721.900.342 | 4
03-01-0972 | UNION DN 25 , PVC , SER. NO. 721.510.108 | 4
03-01-0973 | PE - PIPE CLAMP d = 32 mm , SER. NO. 108 A 6004 | 60
03-01-0974 | SCREW 4.5 x 40 , DIN 96 | 60
03-01-0975 | PLASTIC DOWEL S6 , SER. NO. 117 F 6002 | 60
03-01-0976 | FAN , TYPE DZQ 25/4D,CAPACITY:1100 m3/h, MOTOR:400V,3PH, 50Hz | 10
03-01-0977 | POWER : 55 w , SPEED : 1425 min-1 WITH TROPICAL ISOLATING | 10
03-01-0978 | DURO - VERS B768CHLUPKLAPPE AP25 | 4
03-01-0979 | INSPECTION OF ALL PARTS FROM THE UNIT | 2
CODE | DESCRIPTION | QTY
03-01-0980 | RESIDUAL CHLORINE ANALYZER , CHLORTROL 2" , | 2
CONSISTING OF : PRIMARY UNIT , SECONDARY UNIT AND
CONNECTION CABLE , POWER SUPPLY : 220 V , 50 Hz, OUTPUT
SIGNAL : 4 - 20 m A , METERING RANGE : 0 - 2 mg CL2/L
03-01-0981 | CONNECTION ACCESSORIES WITH PRESSURE READUCING VALVE | 2
03-01-0982 | SAMPLE LINE COMPLETE FOR LINE > DN 300 , | 2
03-01-0983 | CHLORINE COMPARATOR LOVIBOND 1000 METERING RANGE : | 10
0.1 - 5 mg CL2/h ,
03-01-0984 | BREATHING PROTECTION MASK WITH FILTER B IN CARRYING BOX | 20
03-01-0985 | CHLORINE LEAK DETECTOR POWER SUPPLY : 220 V , 50 Hz , | 2
03-01-0986 | SET ACCESSORIES , | 2
03-01-0987 | SET SPARE PARTS , | 2
03-01-0988 | ALARM HORN 220V , 50 Hz , | 2
03-01-0989 | ALARM RESET COMBINATION , | 2
03-01-0990 | PVC - CEMENT 500 cm3 , | 2
03-01-0991 | SPRAY NOZZLE DN 15 , PVC , | 20
03-01-0992 | PVC - PIPE 32 x 1.8 , DN 25 , DIN 8061/62 | 60m
03-01-0993 | SHUT - OFF VALVE R 1" WITH LONGER SPINDLE | 4
03-01-0994 | ELBOW DN 25 , PVC | 20
03-01-0995 | SOCKET DN 25 , PVC | 12
03-01-0996 | TEC , REDUCING DN 25 - 15 - 25 , PVC , | 16
03-01-0997 | REDUCING BUSH DN 25-15 , PVC | 4
03-01-0998 | UNION DN 25 , PVC | 4
03-01-0999 | PE - PIPE CLAMP d = 32 mm , | 60
03-01-01000 | SCREW 4.5 x 40 , DIN 96 | 60
03-01-01001 | PLASTIC DOWEL S6 , | 60
03-01-01002 | FAN , TYPE DZQ 25/4D,CAPACITY:1100 m3/h, MOTOR:400V,3PH, 50Hz | 4
POWER : 55 w , SPEED : 1425 min-1 WITH TROPICAL ISOLATING
FROM CL2
SECTION 2-5: MEDIUM VOLTAGE SWITCH BOARD FOR KARAMA PROJECT
CODE | DESCRIPTION | QTY
11 KV DISTRIBUTION BOARD FOR PROJECT NO. 3 KARAMA TREATMENT PLANT CONTAINS THE FOLLOWING :
03-01-01003 | 630 A , 11KV INCOMMING 1,2 | 2
03-01-01004 | 630 A , 11KV EMMERGINCY 1,2 | 2
03-01-01005 | 630 A , 11KV OUT GOING TO TRANSFORMERS 1, 2 , 3 | 3
03-01-01006 | 630 A , 11KV OUT GOING TO PROJECTS 1,2 | 2
03-01-01007 | NOTE :-
- THE SWITCH BOARD SHOULD INCLUDES ALL THE D.C SYSTEM REQUIPMENT (CHARGER & BATTERIS) & ALL THE PROTECTION RELAYS
- SUPERVISION OF ERECTION THE SWITCH BOARD .
SECTION 2-6: SPARE PART FOR CLARIFIERS IN KARAMA & DOURA PROJECT
CODE | DESCRIPTION | QTY
TYPE : R65 – 1023 – 400 – 4FR
03-01-01008 | DRIVING GEAR , PART NO. = G-M 160-HFZ90 | 6
03-01-01009 | COUPLING , PART NO. = XW 1-110 | 6
03-01-01010 | DRIVING ROLLERS , PART NO. = P-0114/15 | 10
03-01-01011 | GUIDE ROLLERS , PART NO. = P-0114/09 | 10
03-01-01012 | LIMIT SWITCH , PART NO. = BC 1W | 6
03-01-01013 | EST OF RUBBER LEDGES , PART NO. = P-0114/10 , POS 41-44 | 12
03-01-01014 | EST OF RUBBER LEDGES , PART NO. = P-0114/10 , POS 45-47 | 12
03-01-01015 | SLIP RING BODY , PART NO. = KSK 90-8 | 8
03-01-01016 | DISC FOR MIXING , PART NO. = 2 LA 7135/12 | 4
03-01-01017 | SET OF FRICTION WHEEL , PART NO. = 2 LA 7169/16 | 4
03-01-01018 | BEARING , PART NO. = UCP 216 ASAHISEJKO - JAPAN | 24
03-01-01019 | STARS FOR ELECTRIC COUPLINGS , PART NO. = 0 LA 7169/6 | 12
03-01-01020 | WORM GEAR DRIVING MOTOR , PART NO. = 0 LA 7162/2,3 | 2
03-01-01021 | SETS OF RADIAL GASKETS , PART NO. = 0 LA 7169/7 | 12
03-01-01022 | BEARINGS , PART NO. = 0 LA 7169/13 | 12
03-01-01023 | DRIVING ROLLERS , PART NO. = 2 LA 7162/2,3 | 6
03-01-01024 | GUIDE ROLLER , PART NO. = 2 LA 7135/4,6,11 | 2
03-01-01025 | BANDAGE FOR THE ROLLERS , PART NO. = 2 LA 7135/6 | 6
03-01-01026 | DISCS , PART NO. = 2 LA 7135/12 | 24
03-01-01027 | BEARING BUSHED , PART NO. = 2 LA 7135/11 | 48
03-01-01028 | SERVO GEAR MOTOR , PART NO. = 0 LA 7169/16 | 2
03-01-01029 | SET OF RADIAL GASKETS , PART NO. = 0 LA 7169/16 | 4
03-01-01030 | SET OF FRICTION WHEELS , PART NO. = 0 LA 7169/16 | 2
03-01-01031 | BEARING BUSH , PART NO. = 1 LA 7100/8 | 2
03-01-01032 | RUBBER LEDGES , PART NO. = 1 LA 7140/15-23 | EFM 160
03-01-01033 | SLIP RING | 2
03-01-01034 | HOLDERS WITH BRONZE BRUSHES , PART NO. = 0 LA 7169/19 | 18
03-01-01035 | LIMIT SWITCH , PART NO. = 0 LA 7169/21 | 2
SECTION 2-7:DIESEL GENERATORS FOR KARAMA PROJECT
CODE | DESCRIPTION | QTY
03-01-01036 | - O/P VOLTAGE 11 KV | 2
- O/P POWER 1500 KVA , COS ? = 0.9
- SUITABLE FOR OUTDOOR INSTALLATION
- ALL THE NECECCARY ELECTRICAL SWITCH BOARD
- CAPACITY OF STORAGE TANK TO COVER OPERTION FOR 72 HOURS
- COMPRESSED AIR STAETING BY TWO COMPRESSORS ONE DIESEL OPREATED & ONE ELECTRICAL OPRATED
- ENGIN SPEED 1000 R.P.M
SECTION 2-8: SPARE PART FOR KARKH PROJECT
CODE | DESCRIPTION | QTY
TREATED WATER PUMPING STATION , SERIAL NO. C5/56383 , DWG NO. P2003107
03-01-01037 | GELLENK WELLENBAV SERIES G.W.B 190.75 MODEL 01 , FLANG DRIVE BHAFT | 1
03-01-01038 | ELECTRIC ACTVATOR , MOTOR DATA : TYPE 15LBR1 , TIME 15 min , HP 0.6 INS B , 40A , FREQ 50 , 1500 rpm , 400V , FR 42 , CODE 03 | 20
03-01-01039 | BALL BEARING BLL 150 SKF 6230 FOR DWG.NO A0 1432401 ITEM 20 | 10
03-01-01040 | BALL BEARING SKF 7322B FOR DWG.NO A0 1432401 ITEM 53 | 20
03-01-01041 | BALL BEARING 6318 FOR D315LD MOTOR (C1327939) | 10
CODE | DESCRIPTION | QTY
RAW WATER PUMPING STATION ,
03-01-01042 | INTER LOCK RELAY | 20
03-01-01043 | ALARM RELAY | 20
03-01-01044 | DIFFERENTIAL PESSURE AUXICIRY RELAY | 20
03-01-01045 | DIFFERENTIAL PESSURE TIMER RELAY | 20
03-01-01046 | BEARING WATER FLOW TIMER | 20
03-01-01047 | BEARING WATER FLOW AUX REALY | 20
03-01-01048 | PUMP BEARING ALARM RELAY | 20
03-01-01049 | PUMP BEARING TRIP | 20
03-01-01050 | BOOSTER MOTOR TIMER AUXILARY RELAY | 25
03-01-01051 | SUMP LEVEL SLAVE RELAY | 25
03-01-01052 | BOOSTER TEST RELAY | 25
03-01-01053 | PUMP CONTROL PANAL COMPLET | 22
03-01-01054 | TAPER ROLLER THRUST BTING | 15
03-01-01055 | BEARING SPIDER | 4
03-01-01056 | DIAL INDICATOR THERMOMETER | 14
03-01-01057 | INTER MEDIATE SHAFT | 2
03-01-01058 | TOP SHAFT | 2
03-01-01059 | OIL LEVEL GAVGE | 8
03-01-01060 | SPLIT GLAND | 8
03-01-01061 | HEX H.D BOLTS ITEM 63 TO 86-85 | 60
03-01-01062 | HEX H.D BOLTS ITEM 29 TO 83 | 60
03-01-01063 | HEX H.D BOLTS ITEM 62 TO 83,84,64 TO 84 , 87 | 60
03-01-01064 | 500mm PUMP , SERIAL NO. C5/56366/7 | 4
03-01-01065 | IMPELLER | 2
03-01-01066 | PUMP SHAFT | 2
03-01-01067 | WTER MEDIATE SHAFT | 2
03-01-01068 | INTER MEDIATE SHAFT | 2
03-01-01069 | TOP SHAFT | 2
03-01-01070 | PUMP BEARING SLEEVE | 4
03-01-01071 | INTER MEDIAT BEARING SLEEV | 10
03-01-01072 | 60 BORE COUPLING (SLEEVE TYPE) | 6
03-01-01073 | BEL ZONA (1111) | 20 kg
03-01-01074 | BEL ZONA (1321) | 60 kg
FUSE TKF
CODE | DESCRIPTION | QTY
03-01-01075 | 335 A , 80 K ohm , 660 V | 20
03-01-01076 | 315 A , 80 K ohm , 660 V | 20
03-01-01077 | 250 A , 80 K ohm , 660 V | 20
03-01-01078 | CONTACTOR ASED
03-01-01079 | 380 V , 355A , EG-315-1 | 10
03-01-01080 | 380 V , 180A , EG-160-1 | 10
03-01-01081 | 380 V , 110A , EG-80-1 | 10
03-01-01082 | 380 V , 45A , EG-40-1 | 10
03-01-01083 | 110 V , 32A , EG-20 | 10
03-01-01084 | 110 V , 16A , EG-10 | 10
CODE | DESCRIPTION | QTY
VALVES
03-01-01085 | FANCTION : CLARIFIER WATER DRAIN , OPERATED : HAND WHEEL NP/0 FLANG RATING , BODY MATEREAL : CAST IRON , VALVE PLATE : STAINLESS STEEL , SPINDLE MATEREAL : CHROM STEEL , BORE NW : 400mm , NO. OF BOLTE 16 BOLTE SIZE 24 LENGTH WITH SPINDEL = 161 | 10
CODE | DESCRIPTION | QTY
MOTOR FOR CLARIFIER SCRAPER
03-01-01086 | POWER = 3.5 KW , 400V , 1000 rpm , 50 Hz , 3PH , FROM SIZE D132M , FLANGE MOUNTING BOLTE SIZE MR POLES 8 , SHAFT DIA = 38mm , KEY WAY WIDTH 10mm , KEY WAY DEPTH 4mm . | 10
CODE | DESCRIPTION | QTY
CHLORINE RESIDUAL ANALYSER SERLIES66 COMPLETE WITH BUFFER PUMP
M-RANGE 0-10 mg/L , RESOLUTION 0-10 mg/L , RESPONSETIME 30 sec , FLOW THROUGH ELL 500 mL/m , MAX - PRESSURE 2.0 bar , 115/230V , 50/60 HZ , OUT PUT CUYRENT 0.10 mA OR 4-20 mA .
SECTION 2-9 : SPARE PART FOR QADISSYA PROJECT.
CODE | DESCRIPTION | QTY
03-01-01087 | LOW VOLTAGE ELECTRICAL SWITCH BOARD AS DESCRIBED BELOW | 1
1- GENERAL CHARACTERISTICS
A- MATERIAL :
SHEET STEEL ,ANTI-CORROSION
B- SURFACE TREATMENT
ANTI CORROSION COATING THERMAL POLYMERISED POLYSTER
EPOXY POWDER , COLOUR PEIGE
C- BUSBAR INSULATIONS SUPORRTS :
ALL PLASTC PANT WITH STAND FIRE OR ACCESSIVE HEAT CAUSED
CAUSED BY INTERNAL ELEETRIC PHENAENA, AS PER
IEC 695 -201:960, 305/305 FOR SUPPORTS FOR LIVE METAL PARTS
D- BUILDING UP INSTALLATIONS :
THE COMPONENT CAN BE USED TO BUILD SWITCHGEAR ASSEMB-
-LIES IN COMPLAINCE WITH STANDARDS, IEC60439-1, EN60439-1
* RATED INSULATION VOLTAGE FOR BUSBARS 1000V
* RATED CONTINIONS CURRENT 2000A
* PEAK WITHSTAND CURRENT =1PK =187KA
*SHORT TIME WITHSTAND CURRENT =85KA FOR ONE SECOND
*FREQUENCY 50 HZ
E- MAIN BUSBAR SYSTEM: RATED CURRNET=2000 A, CONSISTS OF
THREE PHASES L,1 L,2 L,3, AND N, PE
F- DIMENSIONS :
TOTAL LENGTH SHOULD NOT EXCEED 7.8m , HIGHT SHOULD NOT EXCEED 2.4m WIDTH = 1M
2- COMPONENTS OF THE BOARD :
03-01-01088 | 1- 3 POLE 50 Hz DRAWABLE WITH CHASSIS INCOME FEADER CIRCUIT BREAKER AND BUS COUPLER WITH SPECIFICATION : | 5+1spare
* RATED CONTINIONS CURRENT 2000A at 50 C
* RATED INSULATION VOLTAGE 1000V
* RATED OPERATION VOLTAGE 660V
* MANUAL AND MOTOR CHARGED SPRING STORAGE MECHANISM MOTOR CONTROL VOLTAGE 220V
CLOSING RELEASE CONTROL VOLTAGE 220V
UNDER VOLTAGE TRIP CONTROL VOLTAGE 220V
EACH CB EQUIPED WITH ELECTRONIC PROTECTION UNIT IT HAS THE FOLLOWING FUNCTIONS :
FAULT INDICATION OVER LOAD/ SHORT CIRCUIT , EARTH FAULT , INSTANTINEOUS SHORT CIRCUIT , DIGITAL DISPLAY FOR CURRENT , VOLTAGE ,POWER FACTOR ,FREQUENCY AND POWER.
03-01-01089 | 2- 3 POLE 50 Hz MCCB WITH SPECIFICATIONS : | 6+2spare
* RATED CURRENT 630A AT 50 C
* BREAKING CAPACITY 65 KV
* RATED INSULATION VOLTAGE 750V
* RATED OPERATED VOLTAGE 690V
EACH CB EQUIPED WITH ELECTRONIC PROTECTION UNIT IT HAS THE FOLLOWING FUNCTIONS :
* LONG TIME OVERLOAD PROTECTION WITH INDICATION.
* SHORT TIME SHORT CIRCUIT PROTECTION.
* INSTANTIOUS SHORT CIRCUIT PROTECTION.
* DIGITAL DISPLAY INDICATES THE CURRENT OF THE PHASES .
03-01-01090 | 3- 3 POLE 50 Hz MCCB WITH SPECIFICATIONS : | 2+1spare
* RATED CURRENT 400A at 50 C
* BREAKING CAPACITY 65 KV
* RATED INSULATION VOLTAGE 750V
* RATED OPERATED VOLTAGE 690V
EACH CB EQUIPED WITH ELECTRONIC PROTECTION UNIT IT HAS THE FOLLOWING FUNCTIONS :
* LONG TIME OVERLOAD PROTECTION WITH INDICATION.
* SHORT TIME SHORT CIRCUIT PROTECTION.
* INSTANTIOUS SHORT CIRCUIT PROTECTION.
* DIGITAL DISPLAY INDICATES THE CURRENT OF THE PHASES .
03-01-01091 | 4- 3 POLE 50 Hz MCCB WITH SPECIFICATIONS : | 2
* RATED CURRENT 250A at 50 C
* BREAKING CAPACITY 65 KV
* RATED INSULATION VOLTAGE 750V
* RATED OPERATED VOLTAGE 690V
* RATED CURRENT 250A
EACH CB EQUIPED WITH ELECTRONIC PROTECTION UNIT IT HAS THE FOLLOWING FUNCTIONS :
* LONG TIME OVERLOAD PROTECTION WITH INDICATION.
* SHORT TIME SHORT CIRCUIT PROTECTION.
* INSTANTIOUS SHORT CIRCUIT PROTECTION.
03-01-01092 | 5- 3 POLE 50 HZ 200A MCCB | 2
03-01-01093 | 6- 3 POLE 50 HZ 160A MCCB | 1
03-01-01094 | 7- 3 POLE 50 HZ 100A MCCB | 2
03-01-01095 | 8- 3 POLE 50 HZ 63A MCCB | 4
03-01-01096 | 9- 3 POLE 50 HZ 50A MCCB | 2
03-01-01097 | 10- 3 POLE 50 HZ 25A MCCB | 4
03-01-01098 | 11- PUMP MOTOR SOFT STARTER - SOFT STOP ELECTRONIC STARTER WITH ALL ACCESSORIES SUCH AS FAULT INDICATIONS , METERING , …etc , CAPABLE OF COMMUNICTION WITH COMPUTER ,FOR PUMP MOTOR RATING 250 KW ,3 PHASE ,400V , 50 Hz 1500 RPM | 6+2spare
03-01-01099 | 11- BLOWER SOFT START - SOFT STOP ELECTRONIC STARTER WITH ALL ACCESSORIES SUCH AS FAULT INDICATIONS , METERING , …etc , CAPABLE OF COMMUNICTION WITH COMPUTER ,FOR BLOWER MOTOR RATING 75 KW ,3 PHASE ,400V , 50 Hz 1500 RPM | 2+1spare
NOTE :- SPARE MEANS ADDITIONAL NOT INSTALLED IN THE BOARD
03-01-01100 | ULTRA SONIC FLOWMETER FOR UP WASH FLOW AND FILTERED WATER FLOW DIAMETER 100-300 mm CLAMP ON TYPE . | 14
03-01-01101 | MONITORING PANEL WITH THE METERS AND INDICTIONS AS BELOW | 1
a- 25 FLOW MEASURED VALUES 4-20mA
b- 4 LEVEL MEASURED VALUES 4-20mA
c- 4 PRESSURE MEASURED VALUES 4-20mA
d- 6 INDICATORS FOR HIGH LIFT OLD PUMPING ST. PUMPS
e- 3 INDICATORS FOR HIGH LIFT NEW PUMPING ST. PUMPS
f- 10 INDICATORS FOR LOW LIFT OLD PUMPING ST. PUMPS FOR (d-e-f) PUMP INDICATION RUN OR STOP
g- 10 INDICATORS FOR HT CBs
h- 14 INDICATORS FOR LT CBs IN OLD PUMPING ST.
I- 6 INDICATORS FOR LT CBs IN NEW PUMPING ST.
j- 15 INDICATORS FOR LT CBs IN ROW PUMPING ST. FOR (g-h-I-j) CB INDICATION CLOSE OR OPEN
THE PANEL INCLUDES POWER SUPPLIES TO SUPPLY 24V TO THE INDICATION BULBS ,RELAYS AND INTERNAL CONNECTIONS .
03-01-01102 | k -SPARE BULB FOR ABOVE | 500
03-01-01103 | SUBMERSIBLE PUMP 8KW , 400V , 3PH , 50 Hz , Q= 30L/S , H= 12m , DISCHARGE AND WATER PROOF CABLE ENTRY GLAND , WITH STARTER | 4
CODE | DESCRIPTION | QTY
03-01-01104 | UP WASH PUMP Q= 1500 m3/hr , H = 10m WITH STARTERS , CABLES , FLOWMETERS AND NON RETURN VALVES | 2
03-01-01105 | UP WASH PUMP Q= 1800 m3/hr , H = 10m WITH STARTERS , CABLES , FLOWMETERS AND NON RETURN VALVES | 2
03-01-01106 | OVER HEAD ELECTRIC CRANE TO REPLACE THE EXISTING HIGH LIFT PS NEW PLANT LOAD =4 TON , LIFTING HEAD = 7m , HOISTING SPEED = 3m/min , MICRO HOISTING SPEED = 0.5m/min | 1
03-01-01107 | MONO ELECTRIC/MANUAL CRANE LOAD=2 TOP, LIFTING HEAD =3m , HOISTING SPEED = 2m/min , MICRO HOISTING SPEED = 0.5m/min COMPRESSOR | 1
MEDIUM VOLTAGE SWITCH BOARD
CODE | DESCRIPTION | QTY
11 KV DISTRIBUTION BOARD FOR PROJECT NO. 3 QADISSYA TREATMENT PLANT CONTAINS THE FOLLOWING :
03-01-01108 | 630 A , 11KV INCOMMING 1 (FEEDER) | 1
03-01-01109 | 630 A , 11KV EMMERGINCY 1 (GEN.) | 1
03-01-01110 | 630 A , 11KV OUT GOING TO TRANSFORMERS 1, 2 , 3 | 3
03-01-01111 | 630 A , 11KV OUT GOING SPARE | 1
NOTE :-
- THE SWITCH BOARD SHOULD INCLUDES ALL THE D.C SYSTEM REQUIPMENT (CHARGER & BATTERIS) & ALL THE PROTECTION RELAYS
- SUPERVISION OF ERECTION THE SWITCH BOARD .
SECTION 2-10: SPARE PARTS FOR TAJI RESER: Serial No. C5/56475
Sectional drawing No. P2002552
Taji res. Pumps 250/225 D.E.S.C
CODE | DESCRIPTION | QTY
03-01-01112 | Complete rotating element with motor | 1
03-01-01113 | Gland packing | 4 set
03-01-01114 | Casing spacer ring | 2 set
03-01-01115 | Ball baring | 2 set
03-01-01116 | Half coupling of pump | 2
03-01-01117 | Valve complete with actuators 300 mm | 2
Sectional drawing No. SMC 04/3
03-01-01118 | MANUAL VALVE WITH HANDAL / NEWTON CHAMBER LIMITORQ | 2
03-01-01119 | Pressure switch | 6
03-01-01120 | Differential pressure switch | 6
03-01-01121 | Contractors type ABB 355 Amp voltage coil 110V | 8
03-01-01122 | Contractors type ABB 110 Amp voltage coil 110V | 4
03-01-01123 | Electronic timer type Do/5m-05 | 12
Range 0-1 min.
Operating voltage 110Vac, 8 pins
03-01-01124 | Electronic timer type Do/5m-02 | 12
Range 0-3 min.
Operating voltage 110Vac, 8 pins
Serial No. C5/56471
Sectional drawing No. P223140
Taji res. Pumps 350/300/429 D.E.S.C
CODE | DESCRIPTION | QTY
03-01-01125 | Complete rotating element with motor | 2
03-01-01126 | Gland packing | 3 set
03-01-01127 | Casing spacer ring | 2 set
03-01-01128 | Roll baring | 4
03-01-01129 | Roller baring 7318 | 4
03-01-01130 | Roller baring 6315 | 4
03-01-01131 | Roller baring 1209 | 4
03-01-01132 | Roller baring 23/4LJ | 4
03-01-01133 | Roller baring 1213 | 6
03-01-01134 | Half coupling of pump | 6
03-01-01135 | Valve complete with actuators 400 mm | 6
Sectional drawing No. SMC 04/3
03-01-01136 | MANUAL VALVE WITH HANDAL / NEWTON CHAMBER LIMITORQ | 3
03-01-01137 | Plummer block item(22,23,24) | 6
03-01-01138 | 1 inch Drainage submersible pump | 4
03-01-01139 | H=10m,power=0.75 kW | 1
Basement flooded alarm panel
Serial no.C1880/47 F02
Supply voltage 230Vac
Control supply 110Vac
Modular control L.T.D
03-01-01140 | Complete generator neutral earthing | 1
Supply 400 Vac (N.E.I. REYROLLE BELMOS)
Bus bar rating 400 amp.
03-01-01141 | Earthing relay TYPE 2M6 | 6
400Vac,50Hz,3Ph
coil voltage 110 V
BONAR BRAY LTD SER.NO. 025107-2
SECTION 2-11: EQUIPMENTS FOR FOR . (NORTH , SOUTH , AUB GR. , TAJ.) RES
LIGHTING
03-01-01142 | 6 Feet fluorescent light tube 75/85 watt fitting | 300
03-01-01143 | Mercury lamp 400 watt | 150
03-01-01144 | Mercury lamp 125 watt | 300
03-01-01145 | Complete Emergency light with tube 8 watt | 150
03-01-01146 | 6 Feet fluorescent light tube 75/85 watt | 500
03-01-01147 | 4 Feet fluorescent light tube 40 watt | 400
AIR COOLED IN RES.
CODE | DESCRIPTION | QTY
CARRIER EQUIPMENT
03-01-01148 | UNIT : COMPRESSOR AIR COOLED , TYPE : 06 : ED265 , CAP : 17.7 TAN, 1450 rpm , CYLINDER :6 , INPUT :27KW , REFIGERANT : R22 | 3
03-01-01149 | UNIT : COMPRESSOR AIR COOLED , TYPE : 06 : D/515 , CAP : 10.4 TA - 9.75TAN, 1450 rpm , CYLINDER :6 , INPUT :15.2 KW , REFIGERANT : R22 | 10
03-01-01150 | UNIT : COMPRESSOR AIR COOLED , TYPE : 06 -DA824 , CAP : 5.84 TAN, 1450 rpm , CYLINDER :6 , INPUT :10.8KW , REFIGERANT : R22 | 3
03-01-01151 | REFIGERANT R22 , CYLINDER CAPACITY 13 Kg | 30
AUTOMATIC CYLINDER CHANGE OVER UNIT
CODE | DESCRIPTION | QTY
03-01-01152 | AUTOMATIC CYLINDER CHANGE OVER UNIT | 30
- 240 V AC SUPPLY , 1 PH , 50 Hz
- EACH CHLORINE CYLINDER IS 1000 Kg
- AUTOMATIC & MANUAL OPERATION
- INDICATING LAMPS FOR THE STATE OF EACH CONNECTED CYLINDER ( EMPTY , FULL , STANDBY , IN OPERATION .. ETC )
- ALARM UNIT :-
1- GIVES AUDIABLE ALARM FOR 5 SEC (ADJUSTABLE) IN CASE OF CHANGING CYLINDERS .
2- GIVES AUDIABLE ALARM FOR 30 SEC (ADJUSTABLE) IN CASE OF INSUFFICIENT PRESSURE .
CHLORINE ANALYZER
CODE | DESCRIPTION | QTY
03-01-01153 | RANGE : 0.00 TO 5.00 mg/L TOTAL RESDUAL CHLORINE WALL MOUNTED , 230V AC , 50Hz , ALARMS : ADJUSTABLE LOW & HIGH ALARM SELTINGS SAMPLING TEMP. RANGE : 5 TO 40 C0 , RECORDER 0/P : 4-20mA , DISPLAY : LARGE LED WITH SELF-DIAGNOSTIC MESSAGES , | 20
SECTION 2-12: SPARE PARTS FOR AL- RASHED PLANT
CODE | DESCRIPTION | QTY
THE SWITCH BOARD FOR LOW LIFT PUMPING STATION :
03-01-01154 | INCOMING CIRCUIT BREAKER AND BUS COUPER GENERAL TECHIRCAL DATA : | 3
3-POLE WITH DRAUABLE TYPE ,
* RATED CONTINUOUS CURRENT : 1500A
* RATED OPERATIONAL VOLTAGE : 660V
* MANUAL & MOTOR HARGED SPRING STORAGE MECHANISM : 220V
* GLOSING RELEASE : 220 V
* UNDER VOLTAGE TRIP : 220 V
* OVER LOAD / SHORT CIRCUIT
* INSTANTANEOUS SHORT CET.
* EARTH FANLT
03-01-01155 | PUMP STATER CIRCUIT BREAKER | 6
GENERAL TECHINCAL DATA :
3-POLE WITH DRAUABLE TYPE ,
* RATED CONTINUOUS CURRENT : 400A
* ALL OTHER TECHNICAL DATA PARA 1
03-01-01156 | PUMP STATER DRAING PUMP | 2
GENERAL TECHINCAL DATA :
3-POLE WITH DRAUABLE TYPE ,
* RATED CURRENT : 60A
* ALL OTHER TECHNICAL DATA PARA 1
03-01-01157 | MCCB FOR FLOCUHARS STORTERS (MAIN) | 2
GENERAL TECHINCAL DATA :
3-POLE WITH DRAUABLE TYPE ,
* RATED CURRENT :150A
* ALL OTHER TECHNICAL DATA PARA 1
MCCB FOR SMALL POWER DISTRIBUTION
03-01-01158 | 2 x 30 A | 2
03-01-01159 | 2 x 15 A | 2
SPARE PART FOR PUMPS
CODE | DESCRIPTION | QTY
PUMP TYPE : 10LR-18A IDP , REF : 172000 06 , STAGE :1 , S/N : 1306316 , FLOW : 1000 m3/h , HEAD : 60m+B1303 , LIQUED : CLEAR WATER
03-01-01160 | SHAFT | 3
03-01-01161 | IMPELLER | 3
03-01-01162 | BEARING 6213 ZZ | 20
03-01-01163 | PACKING | 100m
03-01-01164 | CASING GASKAT | 5
03-01-01165 | SHAFT SLEEVE W(0) RING NO.79 | 10set
03-01-01166 | IMPELLER RING W/SET SCREW NO.8 | 10set
03-01-01167 | COMPLETE ROTATING ASSEMBLY CONTIAN (SHAFT , IMPELLER , SHAFT SLEEV , BEARING , IMPELLER RING , PACKING) | 2
03-01-01168 | BEARING 6320 | 6
03-01-01169 | BEARING 6317 | 4
03-01-01170 | SHAFT NUT | 10
03-01-01171 | BEARING LOCK NUT | 10
03-01-01172 | O-RING | 10
CODE | DESCRIPTION | QTY
PUMP TYPE : 300LNN-475 IDP , REF : 17000 06 , STAGE :1 , S/N : 1306326 , FLOW : 1060 m3/h , HEAD : 20m , LIQUED : RAW+B1279 WATER
03-01-01173 | SHAFT | 3
03-01-01174 | IMPELLER | 3
03-01-01175 | CASING GASKAT | 20
03-01-01176 | SHAFT SLEEVE WIL | 20set
03-01-01177 | IMPELLER WEARRINGS | 20set
03-01-01178 | COMPLETE ROTATING ASSEMBLY CONTIAN (SHAFT , IMPELLER , SHAFT SLEEV , BEARING , IMPELLER RING , PACKING) | 3
03-01-01179 | SHAFT NUT | 10
03-01-01180 | BEARING LOCK NUT | 10
03-01-01181 | O-RING | 20
03-01-01182 | SHAFTING BOX PACKING | 10
03-01-01183 | BEARING 6214 | 20
03-01-01184 | BEARING 6322 | 20
03-01-01185 | BEARING 6319 | 20
03-01-01186 | GLAND WITH | 10
03-01-01187 | CLAND RING | 10
CODE | DESCRIPTION | QTY
PUMP TYPE : PDH 1350-45 H.EP : 13/696 PUMP NO. : 2605 , ORDER : 59/602 , FLOW RATE : 960 m3/h , HEAD : 20m , 980 rpm
03-01-01188 | SHAFT | 5
03-01-01189 | IMPELLER | 5
03-01-01190 | SHAFT SLEEVE WIL | 20set
03-01-01191 | IMPELLER WEAR RINGS | 10
03-01-01192 | COMPLETE ROTATING ASSEMBLY CONTIAN (SHAFT , IMPELLER , SHAFT SLEEV , BEARING , IMPELLER RING , PACKING) | 3
03-01-01193 | SHAFT NUT | 10
03-01-01194 | BEARING LOCK NUT | 20
03-01-01195 | O-RING | 20
03-01-01196 | SHAFTING BOX PACKING | 50
03-01-01197 | BEARING 6313 C3 | 30
03-01-01198 | BEARING 6218 | 30
03-01-01199 | BEARING 22318 | 20
03-01-01200 | GLAND | 10
CODE | DESCRIPTION | QTY
03-01-01201 | MIXER FOR AULAM TANK (DIMENSION OF TANK (3.0x2.5x2.5)m) | 8
03-01-01202 | LENGTH OF SHAFT : 2.20m (STAILENESS STEEL) | 8
03-01-01203 | DIMETER OF MIXER : 30 cm (STAILENESS STEEL) | 8
03-01-01204 | MOTOR WITH GEAR BOX WITH CABLE (SPEED 1500/125 rpm) | 8
03-01-01205 | ELECTRICAL CONTROL PANEL CONTAIN : | 10
* MAIN CIRCUIT BREAKER
* MAIN CONTACTOR (COIL 220V)
* THERMAL OVER LOAD
* WITH PROTACTION (PHASE-FALER + SHORT CCT)
* CIRCUIT BREAKER FOR CONTRAL LINE
* PUSH - BOTTOM
* BULBS
SECTION 2-13: SPARE PARTS FOR AL- RASHED & AL-WAHDA PLANT
CODE | DESCRIPTION | QTY
CIRCUIT BREAKER WITH : 3-POLE , MANUAL & MOTOR CHARGED SPRING 220V , UNDER VOLTAGE TRP 220V , OVER LOAD/SHORT CCT , MARTH FAULT
03-01-01206 | 2500A | 3
03-01-01207 | 2000A | 2
03-01-01208 | 1500A | 2
03-01-01209 | 1250A | 4
03-01-01210 | 630A | 10
03-01-01211 | 400A | 5
03-01-01212 | 300 | 10
03-01-01213 | 100A | 10
CONTACTOR
03-01-01214 | 500V , Ith : 200A , AC1 :125A , KW : 75 , Ui : 100V , 50 Hz | 20
03-01-01215 | 500V , Ith : 100A , AC1 :80A , KW : 45 , 50 Hz | 20
03-01-01216 | 500V , Ith : 400A , AC1 :380A , KW : 250 , 50 Hz | 10
03-01-01217 | 500V , Ith : 250A , AC1 :200A , KW : 160 , 50 Hz | 20
03-01-01218 | 500V , Ith : 20A ,COIL : 220V , KW : 5.5 , 50 Hz | 20
OVER LOAD
03-01-01219 | T450 DU 220 - 310A | 20
03-01-01220 | T1 35 DU 80 - 160A | 20
SECTION 2-14: SPARE PARTS FOR 7-NISSAN PLANT
CODE | DESCRIPTION | QTY
03-01-01221 | SCOUR AIR BLOWER | 3
* CAPACITY 3900 m3/h , BACK PRESSURE OF 0.3 bar
* SQUIRREL CAGE INDUCTION MOTOR
* SEMI-FLEXIBLE COUPLING
* COMMON BEDPLATE WITH ANTIVIBRATION SUPPORTS
* 350mm STEEL SUCTION MAIN WITH SILENCER , AIR FILTER , 3NO. 200mm CONNECTION TO THE AIR BLOWERS WITH FLEXIBLE COUPLINGS
* 200mm MS DELIVERY PIPES , WITH FLAP VALVES AND FLEXIBLE COUPLINGS
* BLOWER DIMENTIONS SHOULD BE SUITABLE TO REPLACE THE EXISTING ONE (HIBON DV50)
CODE | DESCRIPTION | QTY
SPARE PARTS FOR DOSING PUMP , TYPE : MC112T 125E5/Z (MILROYAL C) MANUFACTURE : DOSAPRO MILTON ROY
03-01-01222 | HALF COUPLING P.NO. 052 | 3
03-01-01223 | HALF COUPLING P.NO. 052A | 3
03-01-01224 | SEREW P.NO. 435 | 30
03-01-01225 | SHOCK ABSORBER P.NO. 440 | 10set
03-01-01226 | CONNECTING ROD P.NO. 214 | 30
03-01-01227 | CRANK P.NO. 216 | 10
03-01-01228 | TRUNNION P.NO. 237 | 10
03-01-01229 | CROSSHEAD ASSEMBLY P.NO. P | 10
03-01-01230 | CRANK SUPPORT P.NO. 08/C | 5
03-01-01231 | RINSING SPACER P.NO. 006 | 10
03-01-01232 | GUIDE BUSHING P.NO. 007 | 10
03-01-01233 | PLUNGER P.NO. 012 | 10
03-01-01234 | LIQUID END BODY P.NO. 021 | 3
03-01-01235 | GLAND P.NO. 044 | 10
03-01-01236 | PACKING P.NO. 438 | 30set
03-01-01237 | NUT P.NO. A | 10
03-01-01238 | MOUNTING SCREW P.NO. B | 10
03-01-01239 | SCREW P.NO. F | 10
03-01-01240 | VALVE ASSEMBLIES (COMPLETE) P.NO. FIG 7.2A | 10
CODE | DESCRIPTION | QTY
SPARE PARTS FOR DOSING PUMP , TYPE : N27DC - 1 STAGE , COMPANY : DEMPSTER
03-01-01241 | IMPELLER P.NO. 5845-02 | 5
03-01-01242 | WEAR RING P.NO. 5845-08 | 10
03-01-01243 | DISCHARGE BOWL BEARING P.NO. 5845-39B | 20
03-01-01244 | THRUST RING RETAINER P.NO. 5845-82 | 10
03-01-01245 | THRUST RING P.NO. 5485-86 | 10
03-01-01246 | SUCTION BEARING P.NO. 5845-39D | 10
03-01-01247 | BOWL SHAFT P.NO. 5845-06 | 10
03-01-01248 | SHAFT COUPLING P.NO. 438-3-0007 | 20
03-01-01249 | BEARING RETAINER P.NO. 431-3-0304 | 10
03-01-01250 | INSERT P.NO. 400-3-5119 | 50
03-01-01251 | LINE SHAFT P.NO. 427-3-7120 | 10
03-01-01252 | SHAFT SLEEVE P.NO. 429-3-0071 | 30
03-01-01253 | SHAFT COUPLING P.NO. 427-3-0007 | 20
03-01-01254 | TOP SHAFT P.NO. 428-3-7103 | 10
03-01-01255 | STUFFING BOX P.NO. 426-3-0206 | 10
03-01-01256 | BEARING P.NO. 400-3-0160 | 20
03-01-01257 | GLAND P.NO. 426-3-0171 | 20
03-01-01258 | SLINGER P.NO. 426-3-0196 | 20
03-01-01259 | GASKET P.NO. 435-3-0029 | 20
03-01-01260 | STUD P.NO. 900-0-0823 | 60
03-01-01261 | NUT P.NO. 900-0-5014 | 60
03-01-01262 | PACKING RINGS P.NO. 426-3-0079 | 200
03-01-01263 | THRUST BEARING (COMPLET) | 5
CODE | DESCRIPTION | QTY
SPARE PARTS FOR VERTICAL PUMP , TYPE : GL18C , MANUIFACTURER : SPP PUMPS LIMITED , DRAWING NO. 8/508002/2
03-01-01264 | LOCKING ASSEMBLY | 10
03-01-01265 | STUFFING BOX SLEEVE NO. 131 | 20
03-01-01266 | ROUND NUT NO. CB9 | 20
03-01-01267 | ROUND NUT NO. BB9 | 20
03-01-01268 | ROUND NUT NO. A89 | 20
03-01-01269 | THRUST BEARING | 10
03-01-01270 | INTERMEDIATE SHAFT | 10
03-01-01271 | HEAD SHAFT | 5
03-01-01272 | BEARING SLEEVE | 30
03-01-01273 | INTERMEDIATE BEARING (RUBBER) | 30
03-01-01274 | INTERMEDIATE BEARING HOUSING NO. B170 | 10
03-01-01275 | INTERMEDIATE BEARING HOUSING NO. A170 | 10
03-01-01276 | SHAFT COUPLING | 30
03-01-01277 | SPLIT GLAND | 10
03-01-01278 | ROUND NUT | 10
03-01-01279 | STUFFING BOX SLEEVE NO. 45 | 10
03-01-01280 | LOOSE STUFFING BOX | 10
03-01-01281 | PUMP SHAFT | 10
03-01-01282 | BEARING SLEEVE - BOWL | 5
03-01-01283 | BOWL WEAR RING | 5
03-01-01284 | IMPELLER WEAR RING | 10
03-01-01285 | IMPELLER | 5
03-01-01286 | BOWL BEARING (RUBBER) | 10
03-01-01287 | ROUND NUT | 10
CODE | DESCRIPTION | QTY
SPARE PARTS FOR PUMP , TYPE : 300 LNN 475 , MANUIFACTURER : IDP , IDP REF : SP51200011-9/10
03-01-01288 | WEAR RING | 20
03-01-01289 | BEARING HOUSING | 10
03-01-01290 | CASING UPPER HALF | 3
03-01-01291 | BALL BEARING | 10
03-01-01292 | SHAFT | 10
03-01-01293 | IMPELLER (LEFT HANDED & RIGHT HANDED) | 5
03-01-01294 | SLEEVE | 5
03-01-01295 | SHAFT NUT | 20
03-01-01296 | STUFFING BOX HOUSING | 20
03-01-01297 | LANTERN RING | 10
03-01-01298 | STUFFING BOX GLAND | 10
03-01-01299 | GLAND RING | 10
03-01-01300 | V-RING | 30
03-01-01301 | O.RING | 30
03-01-01302 | SCREW | 20
03-01-01303 | LOCK - NUT | 10
CODE | DESCRIPTION | QTY
SPARE PARTS FOR HIGH LIFT PUMPING STATION FOR HORIZONTAL PUMP TYPE : IPM - 44 , MANUIFACTURER : RATEAU
03-01-01304 | BALL BEARING | 20
03-01-01305 | WASHER | 20
03-01-01306 | ADJUSTING RING | 10
03-01-01307 | SEAL | 10
03-01-01308 | IMPELLER NUT | 10
03-01-01309 | BEARING WEB | 10
03-01-01310 | BEARING THRUST SIDE | 10
03-01-01311 | LEFT HARDED IMPELLER | 5
03-01-01312 | RIGHT HARDED IMPELLER | 5
03-01-01313 | IMPELLER RING | 10
03-01-01314 | SLEEVE | 20
03-01-01315 | PACKING | 20set
03-01-01316 | RAMMER | 10
03-01-01317 | BEARING COUPLING SIDE | 10
03-01-01318 | SHAFT | 10
03-01-01319 | COUPLING | 10
CODE | DESCRIPTION | QTY
03-01-01320 | FOR LOW LIFT ELECTRICAL PUMP STARTERS | 30
CONTACTOR TYPE STROMBERG
OKYM SW22
Ith 400A
COIL VOLTAGE 110V
* IF THE TYPE IS NOT AVAILABLE , CHANGE IT BY ANOTHER TYPE WITH THE SAME SPECIFICATIONS AND DIMENTIONS
SPARE PARTS FOR CLARIFIERS
CODE | DESCRIPTION | QTY
03-01-01321 | COMPLETE TIMER , TYPE CHRONO CONTACT 6 WAY NO. 1147 , | 10
240 V , 50 Hz , WITH SPARES FOR 2 YEARS .
03-01-01322 | FOR VALVE TYPE CP1,150mm DIAMETER DIAPHRAGM REF-0002021 089 | 120
03-01-01323 | SLUDGE BLOW-DOWN SOLENOID VALVES , TYPE V301-U-4,240V,50Hz | 30
CLASS BT (LOW VOLTAGE) , HAND CONTROLLED
03-01-01324 | PARTIALIZATION BOX (COMPLETE),TYPE DE40,WITH SPARES FOR 2 YEARS | 30
SPARE PART LIST FOR GAS DOSING SYSTEM 143-040 VOL/TO2
Gs 143 , AS PER DRAWING NO. 125 141-000
CODE | DESCRIPTION | QTY
03-01-01325 | MEASURING TUBE SUPPORT | 20
ITEM (1-1,1-2,1-3,1-4,1-5,1-5-2,1-5-3,1-5-4) PART NO. 12-5138-302P
03-01-01326 | RATE VALVE , PART NO. 12-5100-203P , | 20
03-01-01327 | ITEM (2-1,2-2,2-3,2-4,2-5,2-6,2-7,2-8,2-9,2-10,2-11,2-12,2-13,2-14,2-15,2-16, | 20
2-17,2-18,2-19,2-20,2-21)
03-01-01328 | DIFFERENTIAL PRESSUR REGULATOR PART NO. 12-4258-102P, | 20
ITEM (3-1 - 3-24)
03-01-01329 | SERVO MOTOR , PART NO. 12-5022-401P | 10
03-01-01330 | VACUM METER , PART NO. 12-5112-302P , ITEM (9-1 - 9-4) | 10
03-01-01331 | CHLORINE EVAPORATOR CAP. 230 Kg/h , PRESSURE 14 bar , HEATERS 18KW , TEMRATURE 60 - 65 0C | 3
03-01-01332 | ELECTRICAL HOIST CRANE CAP. 3 TON , SPAN 7.30 m , HIGHT , 4.5m , HOIST SPEED 5m/min | 1
FILTERS FOR 7 NISSAN
CODE | DESCRIPTION | QTY
COMPANY VANNES LEFEBVRE
03-01-01333 | BUTTER FLY VALVE TYPE 310 DIAMETER 600 mm WITH PNEUMATIC ACTUATOR TYPE AP 75-250 WITH ADDITIONAL TWO FLANGES OF 600 mm . | 14
03-01-01334 | BUTTER FLY VALVE TYPE 310 DIAMETER 450 mm WITH PNEUMATIC ACTUATOR TYPE AP 75-200 WITH ADDITIONAL TWO FLANGES OF 450 mm . | 28
03-01-01335 | BUTTER FLY VALVE TYPE 310 DIAMETER 300 mm WITH PNEUMATIC ATNATOR TYPE AP 50-160 WITH ADDITIONAL TWO FLANGES OF 300 mm . | 14
03-01-01336 | VIKING JONSON JOINT 600 m | 28
03-01-01337 | VIKING JONSON JOINT 450 m | 56
03-01-01338 | VIKING JONSON JOINT 300 m | 28
03-01-01339 | VALVE 100 mm | 14
03-01-01340 | VALVE 50 mm | 14
03-01-01341 | NOZZLES TYPE D.20-CODE 60 436 WITH JOINTS Ø 28 x 40 – 2 mm THICK – CODE 60463 . | 92000
03-01-01342 | PARTIALIZATION BOX TYPE DE.40 COMPLETE WITH ALL ACCESSORIES . | 14
03-01-01343 | SCOUR AIR BLOWER (HIBBON) TYPE DV50 COMPLETE WITH MOTOR AND STARTER (Q = 3900 m3/h , H = 0.3 bar ) . | 3
03-01-01344 | DESK AND WASHING AUTOMATION CABINET CONSIST OF THE FOLLOWING :- | 14
a- CYCLOMATIC TYPE SEM 70/2.
b- SOLENOID VALVE M2T301 .
c- HEAD LOSS METER .
d- ON/OFF SWITCH .
e- SIGNAL LAMPS .
f- AIR VALVES .
g- ALL CONTROL EQUIPMENTS FOR OPERATIONS .
03-01-01345 | GATE VALVE 450 mm | 3
03-01-01346 | GATE VALVE 400 mm | 3
03-01-01347 | NON – RETURN VALVE 400 m | 3
03-01-01348 | NON – RETURN VALVE 200 m | 3
03-01-01349 | IRON PIPE 600 mm | 300 m
03-01-01350 | IRON PIPE 300 mm | 200 m
03-01-01351 | IRON PIPE 350 mm | 70 m
03-01-01352 | IRON PIPE 450 mm | 80 m
03-01-01353 | IRON PIPE 900 mm | 50 m
03-01-01354 | COPPER PIPE 8 mm | 400 m
03-01-01355 | COPPER PIPE 10 mm | 600 m
03-01-01356 | COPPER PIPE 12 mm | 400 m
03-01-01357 | CONNECTING FITTINGS 8 mm | 200
03-01-01358 | CONNECTING FITTINGS 10 mm | 200
03-01-01359 | CONNECTING FITTINGS 12 mm | 200
- COMPRESSED AIR STAETING BY TWO COMPRESSORS ONE DIESEL OPREATED & ONE ELECTRICAL OPRATED
- ENGIN SPEED 1000 R.P.M
HIGH LIFT PUMPING STATION FOR 7 NISSAN
CODE | DESCRIPTION | QTY
03-01-01360 | HIGH LIFT PUMPING STATION | 1
ELECTRICAL SWITCH BOARD (7.2 Kv)
DIMTION : L x W x H
323x100x224
THE BOARD CONTAIN 4 FOR CUBICLES WITH DRAWABLE CIRCUIT BREAKERS SF6 :-
2 IN COMERS 630 A
1 OUT GOING 630 A
1 BUS COUPLER 1250 A
WITH PROTECTION RELAYS (S.CT. , THERMAL , UNDER VOLTAGE ) AND MEASURMENTS (VOLTS , AMPS , SWITCHS , ETC )
THE BOARD TO BE MATCHED WITH EXISTING EQUIPMENT.
03-01-01361 | ELECTRICAL SWITCH BOARD (7.2 Kv) | 1
DIMTION : L x W x H
370x100x224
THE BOARD CONTAIN 4 FOR CUBICLES WITH DRAWABLE CIRCUIT BREAKERS SF6 :-
2 IN COMERS 630 A
2 OUT GOING 630 A
1 BUS RISER
WITH PROTECTION RELAYS (S.CT. , THERMAL , UNDER VOLTAGE ) AND MEASURMENTS (VOLTS , AMPS , SWITCHS , ETC )
THE BOARD TO BE MATCHED WITH EXISTING EQUIPMENT.
SPARES CIRCUIT BREAKERS FOR THE ABOVE ITEM
03-01-01362 | 630 A | 2
03-01-01363 | 1250 A | 1
CODE | DESCRIPTION | QTY
03-01-01364 | SF6 CONTACTOR 7.2 Kv , 300 A , TYPE SFC320 , FIXED TYPE , MAIN COIL VOLTAGE 110V A.C | 14
Cr 16.5 KA , EFFECT 6.6 KA , 16 AUXILLARY CONTACTS , DIMENTIONS L x W x H 56x54x40
SECTION 2-15: SUBMERSIBLE PUMP
03-01-01365 | SUBMERSIBLE PUMP 1" SINGLE PHASE FOR TREATED WATER WITH STARTER | 25
03-01-01366 | SUBMERSIBLE PUMP 1" SINGLE PHASE FOR RAW WATER WITH STARTER | 10
03-01-01367 | SUBMERSIBLE PUMP 2" SINGLE PHASE FOR TREATED WATER WITH STARTER | 25
03-01-01368 | SUBMERSIBLE PUMP 2" SINGLE PHASE FOR RAW WATER WITH STARTER | 10
03-01-01369 | SUBMERSIBLE PUMP 2" FOR TREATED WATER WITH STARTER THREE PHASE | 80
03-01-01370 | SUBMERSIBLE PUMP 2" FOR RAW WATER WITH STARTER THREE PHASE | 20
03-01-01371 | SUBMERSIBLE PUMP 3" FOR TREATED WATER WITH STARTER THREE PHASE | 60
03-01-01372 | SUBMERSIBLE PUMP 3" FOR RAW WATER WITH STARTER THREE PHASE | 50
03-01-01373 | SUBMERSIBLE PUMP 4" FOR TREATED WATER WITH STARTER THREE PHASE | 50
03-01-01374 | SUBMERSIBLE PUMP 4" FOR RAW WATER WITH STARTER THREE PHASE | 30
COMPLETE SPARE PARTS FOR ALL SUBMERSIBLE PUMPS
SECTION 2-16: SPARE PART FOR RAW WATER STATION
CODE | DESCRIPTION | QTY
03-01-01375 | COMPLETE COOLING PUMPS WITH MOTOR ,Q = 60m3/h H = 20m WITH MOTOR = 5.5 KW , 400V . | 4
03-01-01376 | TEM P4005 A/B RPS3 | 4
03-01-01377 | P5005 A/B RPS4 WITH COMPLET SPARE PART FORT BOTH AS FOLLOWS | 4
03-01-01378 | SHAFT | 20
03-01-01379 | IMPLLER | 20
03-01-01380 | SHAFT SLEEVE | 40
03-01-01381 | ROTATING | 40
03-01-01382 | MECHANICAL SEAL SLEEVE | 40
03-01-01383 | STATIONARY RING | 20
03-01-01384 | SET OF COVPLING PADS | 100
03-01-01385 | SET OF BEARING | 20
SPARE PART FOR RAW WATER PUMPING STATION , MAIN PUMPS :
03-01-01386 | TOP SHAFT | 30
03-01-01387 | SHAFT SLEEVE | 100
03-01-01388 | BAAVING BUSH | 250
03-01-01389 | IMPELLER BEARING SLEEVE | 20
03-01-01390 | ADJUSTING NUT | 10
03-01-01391 | WASHERS (2PER SET) | 40SET
03-01-01392 | WASHERS FOR BEARING NUT | 40
03-01-01393 | COMPLETE MUFF COUPLING WITH SCREWS | 100SET
03-01-01394 | IMPELLER (1ST - 2ND) | 50
03-01-01395 | 1ST STAGE PUMP BOWEL WITH RING & SCREW | 10
03-01-01396 | 2ND STAGE PUMP BOWEL WITH RING & SCREW | 10
03-01-01397 | SET OF RADIAL AND THRUST BEARING | 20SET
03-01-01398 | IMPELLER SHAFT | 20
03-01-01399 | THRUST BEARING CARRIER (COMPLETE WITH BEARING & WASHERS AND ACCESSORY) | 10
03-01-01400 | BEARING COVER | 10
03-01-01401 | IMPELLER BEARING SLEEVE | 100
03-01-01402 | SHAFT TUNNEL T0 BE (UPPER) | 20
03-01-01403 | GREASE REGULATOR | 20
03-01-01404 | THRWER | 50
03-01-01405 | GLAND FLANGE | 20
03-01-01406 | FOLLOWER , SPLIT | 20
03-01-01407 | SHAFT TUNNEL T0 BE (MIDDLE) | 25
03-01-01408 | SHAFT TUNNEL T0 BE (LOWER) | 25
03-01-01409 | BEARING NUT | 25
03-01-01410 | SCREW FOR ADJUSTING MLT | 50
03-01-01411 | SEPARATION WASHER | 50
03-01-01412 | FILTER (ISIS H) (DN 50) | 5
03-01-01413 | AXIAL AND RADIAL BEARING FOR MOTOR VF 180 - 27 TYPE RNCB500 2PER SET+B1525 | 10 SET
03-01-01414 | AXIAL AND RADIAL BEARING FOR MOTOR VF 460 - 31 TYPE RNCB560 2PER SET | 20 SET
03-01-01415 | SPACER RING FOR COUPLING PUMP SIDE | 10
03-01-01416 | LOCATING COLLAR FOR BEARING | 10
03-01-01417 | BEARING ADAPTER SLEEVE | 10
03-01-01418 | BEARING SLEEVE | 250
CODE | DESCRIPTION | QTY
SPARE FOR WINFLUX COPLING INCLUDE ;
03-01-01419 | SPNING FOR COUPLING (GRID) | 20
03-01-01420 | SEAD RING | 20
03-01-01421 | HALF COVER | 20
03-01-01422 | GASKET | 20
03-01-01423 | CAP SCREW AND NUTS (COMPLETE FOR EACH) | 20
03-01-01424 | GLAND PACKING | 1000 m
03-01-01425 | SCREW AND MALE FEMALE UNIONS | 50
03-01-01426 | VALVE | 100
03-01-01427 | UNION ELBOW 1/2" | 50
03-01-01428 | UNION FITTING 1 1/2" | 50
03-01-01429 | UNION FITTING 1/2" | 100
03-01-01430 | REDUCED NIPPLE FOR BEARING | 25
03-01-01431 | INTERMEDIATE BEARING | 20
03-01-01432 | TOP BEARING | 20
03-01-01433 | COUPLING RING SPLIT | 20
03-01-01434 | INTER STAGE SLEEVE | 15
03-01-01435 | IMPELLER NUT WITH SCREW | 20
03-01-01436 | STUD | 500
03-01-01437 | NUT | 500
03-01-01438 | SCREW | 500
03-01-01439 | LUBRICATING PIPE FOR IMPLLER | 20
03-01-01440 | REDUCED NIPPLE FOR IMPLLER | 20
03-01-01441 | BELL MOUTH WITH RING & SCREW | 10
03-01-01442 | CASING WEAR RING | 10
03-01-01443 | CONNECTING PIECE | 10
START RAW WATER PUMPS ;
03-01-01444 | INTERMEDIATE SHAFT | 5
03-01-01445 | TOP SHAFT | 10
03-01-01446 | IMPELLER SHAFT | 10
03-01-01447 | 1ST STAGE IMPELLER | 10
03-01-01448 | 2ND STAGE IMPELLER | 10
03-01-01449 | ADJUSTING NUT | 5
03-01-01450 | INTERMEDIATE BEARING SLEEVE | 20
03-01-01451 | IMPELLER BEARING SLEEVE | 20
03-01-01452 | SET OF RADIAL & THRUST BEARINGS (2 PER SET) | 10SET
03-01-01453 | THRUST BEARING COVER (COMPLETE WITH BEARING & WASHERS AND ACCESSORY | 10
03-01-01454 | BEARING COVER | 10
03-01-01455 | BEARING BUSH | 50
03-01-01456 | COMPLETE MUFF COUPLING WITH SCREWS (2 PER SET) | 20SET
03-01-01457 | SHAFT SLEEVE | 20
03-01-01458 | WASHERS (2 PER SET) | 10
03-01-01459 | WASHERS FOR BEARING NUT | 5
03-01-01460 | 1ST STAGE PUMP BOWEL WITH RING & SCREW | 5
03-01-01461 | 2ND STAGE PUMP BOWEL WITH RING & SCREW | 5
03-01-01462 | SHAFT TUNNEL TO BE (UPPER) | 10
03-01-01463 | SHAFT TUNNEL TO BE (MIDDLE) | 10
03-01-01464 | SHAFT TUNNEL TO BE (LOWER) | 10
03-01-01465 | GREASE REGULATOR | 10
03-01-01466 | THROWER | 10
03-01-01467 | GLAND FLANGE | 10
03-01-01468 | FOLLOWER , SPLIT | 10
03-01-01469 | BEARING NUT | 10
RAW WATER PUMPING STATION
(KPS1 , RPS1 , RPS3 , RPS4)
CODE | DESCRIPTION | QTY
SELF ACTUATED CONTROL VALVE DN 500 PN10
DWG NO. 3670 - 00 - 2720 - 4+B1678 - 003
03-01-01470 | O-RING R7 , PART NO. 7,12,13,15 | 1000 m
03-01-01471 | O-RING R71, PART NO. 10 | 200
03-01-01472 | O-RING R37 , PART NO.19 | 200
03-01-01473 | O-RING R22 , PART NO. 23 | 200
03-01-01474 | LIMIT SWITCH (TELEMECANIQUE) , PART NO. 27 | 250
03-01-01475 | PLATE , PART NO. 11 | 10
03-01-01476 | PISTON , PART NO. 9 | 2
03-01-01477 | SEAT , PART NO.8 | 20
03-01-01478 | CYLINDER , PART NO.17 | 2
03-01-01479 | NEEDLE VALVE 1/2" NPT FEMALE , PART NO. 20 | 200
03-01-01480 | DEGASING TRP 1/4" GAS , PART NO. 22 | 100
03-01-01481 | DEGASING TRP 3/8" GAS , PART NO. 28 | 100
03-01-01482 | BALL VALVE 1/2" NPT FEMALE , PART NO. 30 | 350
03-01-01483 | DISC , PART NO. 24 | 10
03-01-01484 | AIR TANK CHAR LATTE 2001 , PART NO. 29 | 2
03-01-01485 | FITTING 1/2" GAS x 1/2" NPT FEMAL , PART NO. 28 | 100
03-01-01486 | FITTING 1/2" GAS FEM x 1/2" NPT FEMAL , PART NO. 42 | 100
03-01-01487 | DOUBLE VALVE 1/2" , PART NO. 43 | 100
03-01-01488 | FITTING 1/2" NPT MALE , PATR NO. 36 | 100
03-01-01489 | TEE 1/2" NPT FEMALE , PART NO. 44 | 100
03-01-01490 | SCREW CHC.M20 - 55 , PART NO. 16 | 50
03-01-01491 | CLIPS , PART NO. 14 | 10
03-01-01492 | FIXING CLIPS SEGMET , PART NO. 31 | 20
03-01-01493 | BOLT HM 8-25 , PART NO. 32 | 50
SELF ACTUATED CONTROL VALVE DN 700 PN10 , DISCHARGE PUMPS
DWG NO. 3670 - 00 - 2770 - 4 - 55 - 001
03-01-01494 | SEAT , PART NO.90 | 50
03-01-01495 | PISTON , PART NO. 10 | 2
03-01-01496 | O-RING R7 , PART NO. 8,12,14,15 | 1000m
03-01-01497 | O-RING R83, PART NO. 11 | 100
03-01-01498 | PLATE , PART NO. 13 | 25
03-01-01499 | CLIPS , PART NO. 16 | 20
03-01-01500 | SCREW M8-20 , PART NO. 17 | 25
03-01-01501 | FIXING CLIPS SEGMET , PART NO. 18 | 25
03-01-01502 | SCREW CHC.M20 - 60 , PART NO. 19 | 50
03-01-01503 | CYLINDER , PART NO.20 | 4
03-01-01504 | UNION 1/2" NPT MALE , PART NO. 21 | 10
03-01-01505 | O-RING R43, PART NO. 24 | 50
03-01-01506 | O-RING R22, PART NO. 26 | 100
03-01-01507 | DISC , PART NO. 27 | 25
03-01-01508 | AIR TANK CHAR LATTE 3001+B1741 , PART NO. 32 | 2
VENDOR : GUICHON SA : 73104 ALXLESBAINS :-
03-01-01509 | COMPLETE CHECK VALVE PN 16 ND500 HOUSING | 4
03-01-01510 | COMPLETE CHECK VALVE PN 16 ND700 HOUSING | 6
03-01-01511 | SPARE PART FOR THE VALVES ABOVE :-
03-01-01512 | COVER FOR BOTH SIDE FOR DN700 | 100
03-01-01513 | COVER FOR BOTH SIDE FOR DN500 | 40
03-01-01514 | SCREWS FOR BOTH SIDE FOR DN500 | 250
03-01-01515 | SCREWS FOR BOTH SIDE FOR DN700 | 100
CODE | DESCRIPTION | QTY
03-01-01516 | DISC RING FOR DN500 | 20
03-01-01517 | DISC RING FOR DN700 | 100
03-01-01518 | RING RETAINING WASHER FOR DN500 | 50
03-01-01519 | RING RETAINING WASHER FOR DN700 | 100
03-01-01520 | AXLE FOR DN500 | 50
03-01-01521 | AXLE FOR DN700 | 10
03-01-01522 | FREE AXLE FOR DN500 | 10
03-01-01523 | FREE AXLE FOR DN700 | 200
03-01-01524 | O-RING FOR BOTH SIDE FOR DN500 | 50
03-01-01525 | O-RING FOR BOTH SIDE FOR DN700 | 200
03-01-01526 | OPENING INDICATOR (HANDLE) SHAFT AND LEVER OUTLET FOR DN500 | 10
03-01-01527 | OPENING INDICATOR (HANDLE) SHAFT AND LEVER OUTLET FOR DN700 | 20
03-01-01528 | SCREWS FOR DN500 | 100
03-01-01529 | SCREWS FOR DN700 | 500
MECAFRANCE 10/18 RUE DU LANGNE DOC. ZADES BETHUNES
BALL VALVES
03-01-01530 | BALL VALVE RSST FLANGED ENDS PN16 DN2" | 50
03-01-01531 | BALL VALVE RSST FLANGED ENDS PN16 DN2" REDUCED BORE | 25
03-01-01532 | BALL VALVE RSST FLANGED ENDS PN16 DN4" REDUCED BORE | 15
03-01-01533 | BALL VALVE RSST CBB (NPT) DN1" REDUCED BORE | 25
SONIC AIR EXHAUST VALVE (ERIKS-S.AR.L)
03-01-01534 | SONIC AIR EXHAUST VALVE | 10
03-01-01535 | AIR INLET VALVE | 10
PONT-A- MOUSSON S.A 54700 , SERVICES TECHNIQES BP45
| FLOAT VALVE EQUILIBRATED VALVE TYPE 1DN80 (WITH THE FLOAT) | 5
| ACTUATED GATE VALVE EURO 16DN200 | 5
ERIKS - 52 AVENUE DES FRERES LUMERE
03-01-01536 | CAST IRON BODY BJ 5156 LENGTH PN16 RF FLANGED. | 5
03-01-01537 | FORGED GATE VALVE AP1 602-800/b DWG. NO. FIG 2519/610 , (1.5") | 25
03-01-01538 | GLOBE VALVE PN16 DWG. FIG. 3210 | 5
FORGED GLOBE VALVE AP1 602-800/b DWG. NO. FIG 2049/650
SELF AETUATED CONTRAL VALVE
03-01-01539 | PRESSURE CONTROL VALVE DOWN FLOW STABILISER DN 80-PN16 | 5
03-01-01540 | PRESSURE CONTROL VALVE HEADUP FLOW STABILISER DN 80-PN16 | 5
03-01-01541 | O-RING R21 | 10 SET
03-01-01542 | O-RING R27 | 10 SET
03-01-01543 | O-RING R46 | 10 SET
03-01-01544 | O-RING R38 | 10 SET
03-01-01545 | O-RING R12 | 10 SET
03-01-01546 | O-RING R22 | 10 SET
03-01-01547 | O-RING R71 | 10 SET
03-01-01548 | O-RING R59 | 10 SET
03-01-01549 | O-RING R52 | 10 SET
03-01-01550 | O-RING R14 | 10 SET
03-01-01551 | SWING CHECK VALVE PN16 DWG.FIG.3403 CODE SB : CCOL | 5
HERION
03-01-01552 | SOLENIOD VALVE 2/2 WAY ND 25 | 50
03-01-01553 | SOLENIOD VALVE ND 40 2/2 WAY | 50
LOW VOLTAGE CIRCUIT BREAKER
03-01-01554 | MG. 630A | 5
03-01-01555 | RAW WATER FLOW TO NETWORK FULL SCALL 36000 m3/h PC2000 | 4
03-01-01556 | RAW WATER MANIFOLD PRESSURE FULL SCALL 0-100 m.w.c PC2000 | 4
03-01-01557 | RESET TOTAL FLOW UNIT m3 x 100 | 4
03-01-01558 | TOTAL FLOW UNIT m3 x 100 | 4
SECTION 2-17: GENERATOR
CODE | DESCRIPTION | QTY
03-01-01559 | GENERATOR 1750 KVA H.T : | 1
POWER >= 1575 KW
ENG. POWER (CONTINUOUS AT 550C)
TYPE OF STARTING : AIR STARTING
TYPE OF GOVERNER MECH. / HYDRAULIC
AMBIENT TEMP. 550C
TYPE OF RADIATOR : TROPICAL
COOLING : WATER
CLASS OF INSULATION : F
STARTING : DIESEL COMPRESSOR + ELECTRIC COMPRESSOR
ELECTRIC BATTERY CHARGER 24 , 70 A
LO PRESSURE SHUTDOWN PROTECTION
HI WATER TEMP. SHUTDOWN PROTECTION
OVER SPEED SHUTDOWN
DAILY FEED TANK 48h
OIL DRAIN PUMP
SPEED : 1000 rpm
MEASURMENT V , A , COS , KVAR , HZ , KW , SPEED
AUTO. CHANGE OVER SWITCH
BATTERY : NI - CD BATTERIES
ELECTRIC PROTECTION , EARTH FAULT , PHASE REVERSE , SHORT ECT.
SET OF ENGINE SPARE PARTS :
03-01-01560 | INJECTOR NOZZEL | 10
03-01-01561 | INJECTOR WASHER | 20
03-01-01562 | AIR FILTER ELEMENT | 6
03-01-01563 | RADIATOR CAP. | 2
03-01-01564 | WATER PUMP KIT. | 1
03-01-01565 | WATER HOSE | 4
03-01-01566 | CORRUGALE HOSE | 2
03-01-01567 | CRANK SHAFT BEARING | 4
03-01-01568 | CONNECTING ROD | 5
CODE | DESCRIPTION | QTY
03-01-01569 | GENERATOR 750 KVA L.T : | 1
POWER > 690 KW
ENG. POWER (CONTINUOUS AT 550C) >= 690 KW
TYPE OF STARTING : AIR STARTING
TYPE OF GOVERNER MECH. / HYDRAULIC
AMBIENT TEMP. 550C
TYPE OF RADIATOR : TROPICAL
COOLING : WATER
CLASS OF INSULATION : F
STARTING : DIESEL COMPRESSOR + ELECTRIC COMPRESSOR
ELICTRIC BATTERY CHARGER 24 , 70 A
LO PRESSURE SHUTDOWN PROTECTION
HI WATER TEMP. SHUTDOWN PROTECTION
OVER SPEED SHUTDOWN
DAILY FEED TANK 48h
OIL DRAIN PUMP
SPEED : 1000 rpm
MEASURMENT V , A , COS , KVAR , HZ , KW , SPEED
AUTO. CHANGE OVER SWITCH
BATTERY : NI - CD BATTERIES
ELECTRIC PROTECTION , EARTH FAULT , PHASE REVERSE , SHORT ECT.
SET OF ENGINE SPARE PARTS :
03-01-01570 | INJECTOR NOZZEL | 10
03-01-01571 | INJECTOR WASHER | 20
03-01-01572 | AIR FILTER ELEMENT | 6
03-01-01573 | RADIATOR CAP. | 2
03-01-01574 | WATER PUMP KIT. | 1
03-01-01575 | WATER HOSE | 4
03-01-01576 | CORRUGALE HOSE | 2
03-01-01577 | CRANK SHAFT BEARING | 4
03-01-01578 | CONNECTING ROD | 5
SECTION 2-18: COMPACT UNIT
03-01-01579 | CONTAINERIZED PREMOUNTED WATER TREATMENT PLANT
NOS : 6+B1672
PLANT CAPACITY 200 m3/hr
ELECTRIC POWER 400 V+ 10% , 50 Hz , 3-PHASE A.C.
RAW WATER PUMPS
NUMBER : 2
CAPACITY : 260 m3/h
HEAD : 20m
HORIZONTAL , CENTRIFUGAL END - SACTION TYPE WITH SPEED 1450 rpm , GLAND TYPE
NPS Hr : 2.6 m
FILTER LOADING PUMP
NUMBER : 2
CAPACITY : 200 m3/h
HEAD : 50m
HORIZONTEL , CENTRFUGAL END SUCTION TYPE WITH SPEED 1450 R.P.M , GLAND TYPE .
FLOCCULATION
RETENTION PERIOD NOT LESS THAN 14.5 MINUTES
SEDIMENTATION
HYDRAUTIC SURFACE LOAD : 1.0 m3/m2/h
THICKNESS OF THE TANK PLATE : 6 mm
FILTERATION
FILTRATION VELOCITY NOT MORE THAN : 9.0 m/hr
DRINKING WATER OUTLET PRESSURE : 50 - 60 METER
THICKNESS OF THE FILTER PLATE : 10 mm
THICKNESS OF THE DISHED END OF
FILTERS TO BE : 12 mm
TESTING PRESSURE : 10 bar
GENERAL
1- THE PREFABRICATED PLANT IS DESIGNED TO PRODUCE POTABLE WATER FROM RIVER , LAKE ,
THE PLANT IS DESIGNED FOR EXTREMELY EASY ASSEMBLY AND DISASSEMBLY IN REMOTE AREAS , I.E. ALL PROCESS EQUIPMENTS ARE SKID MOUNTED IN CONTAINER UNITS INCLUDING TANKS , PUMPS , FILTERS , HYDROPHORES , ELECTRICAL PANED AND DOSING EQUI
2- THE DRINKING WATER MEETS THE REQUIREMENTS OF THE ( INTERNATIONAL STANDARDS FOR DRINKING WATER )
( WORLD HEALTH ORGANISATION) .
DISINFECTION
CHLORINE GAS IS USED FOR DISINFECTION , FIRST , BY SHOCK CHLORINATION , SECOND , ACONTINUOUS CHLORINATION IS FORESEEN TO AVOID GERMINATION IN THE DISTRIBUTION NETWORK .
03-01-01580 | NUMBER OF UNITS : 2
CAPACITY : 2000 g/h
ENCLUDING : 2 CYLINDERS WITH 65 Kg ,
2 BOOSTING PUMPS CAPACITY 4 m3/h , HEAD : 80 METER
CHEMICAL DOSING SYSTEM
a- ALUMINIUM SULPHATE PUMPS
CAPACITY : 200 L/h
HEAD : 6 bar
NUMBER : 2
b- ALUMINIUM SULPHATE TANK
CAPACITY : 1000 L
NUMBER : 2
INCLUDED ONE FLASH MIXER FOR EACH TANK .
SECTION 2-19: SPARE PARTS LIST FOR (ABA ACAS) CRAINS OF ALL RES.
CODE | DESCRIPTION | QTY
3 , 5 , 7.5 TONE
03-01-01581 | ROPE (SLOW , HIGH) | 4
03-01-01582 | ROPE GUIDE COMPLETE | 4
03-01-01583 | PRESSURE RING COMPLETE | 4
03-01-01584 | BARREL ROLLER RACE | 4
03-01-01585 | 1st REDUCTION GEAR BALL BEARING | 4
03-01-01586 | COMPLETE THARST BEARING | 4
03-01-01587 | ROLLER BEARING WITHOUT INNER RING | 4
03-01-01588 | FELT SEAL HOUSING (BRAKE END) | 4
03-01-01589 | CIRCLIP FOR BRQKE END PLATE | 4
03-01-01590 | ROLLER DISC BRAKE (COMPLETE) | 4
03-01-01591 | HOOK BLOCK ASSEMBLY COMPLETE | 4
03-01-01592 | BRAKE DISC AND LINING | 4
03-01-01593 | FELT SEAL HOUSING (PINION END) | 4
03-01-01594 | SHAFT ROLLER BEARING | 4
SECTION 2-20: M.V. POWER FACTOR CORRECTION EQUIPMENT FOR RAW WATER PUMPING STATION
CODE | DESCRIPTION | QTY
03-01-01595 | * SUPPLY 11KV POWER FACTOR CORRECTION EQUIPMENT TO IMPROVE THE EXCISTING P.F. TO 0.93 | 4 sets
* THE EQUIPMENT SHOULD BE SUITABLE TO BE CONNECTED IN PARALLEL WITH THE EXCISTING MOTOR AS BELOW
KSP1 : 8x840 KW + 2x460KW
RSP1 : 8x840 KW + 2x460KW
RSP3 : 4x840 KW + 2x460KW
RSP4 : 6x840 KW + 2x460KW
* ALL THE REQVIRED CONNECRING CABLES & ACCESSARIES
* SUPERVISION OF INSTALLATION
SECTION 2-21: MEDIUM VOLTAGE SWITCH BOARD FOR QADISSYA PROJECT
CODE | DESCRIPTION | QTY
11 KV DISTRIBUTION BOARD FOR PROJECT NO. 3 QADISSYA TREATMENT PLANT CONTAINS THE FOLLOWING :
03-01-01596 | 630 A , 11KV INCOMMING 1 (FEEDER) | 1
03-01-01597 | 630 A , 11KV EMMERGINCY 1 (GEN.) | 1
03-01-01598 | 630 A , 11KV OUT GOING TO TRANSFORMERS 1, 2 , 3 | 3
03-01-01599 | 630 A , 11KV OUT GOING SPARE | 1
NOTE :-
- THE SWITCH BOARD SHOULD INCLUDES ALL THE D.C SYSTEM REQUIPMENT (CHARGER & BATTERIS) & ALL THE PROTECTION RELAYS
- SUPERVISION OF ERECTION THE SWITCH BOARD .
SECTION 2-22; SPARE PARTS FOR LAB.
CODE | DESCRIPTION | QTY
03-01-01600 | FUME HOOD BENCH TYPE FOR , NEED , CONSTANT VOLUME BY PASS, FOR HANDLING ACIDS AND RAIDOACTIVE ISOTOPES , NON METALLIC COMPLETE WITH PLOWER AND ACCESSORIES . | 2
03-01-01601 | DPD TABLETS NO.1 | 5000tab
03-01-01602 | SULFANILAMIDE (ANALAR) | 1kg
03-01-01603 | SOLOCROME CYNENE R (AR) OR ERIOCHROME CYNENE R(AR) | 1kg
03-01-01604 | ERIOCHROME BLACK T | 500g
03-01-01605 | RED MERCURIC IODIDE (AR) | 1kg
03-01-01606 | MUREXIDE | 500g
03-01-01607 | FOLOCCULATORS (FLOCUMATIC) | 2
a. ACCEPTS 6 SAMPLES
b. ELECTRICAL SUPPLY (220-230V) , 50 Hz , 200W
c. BUILT IN ILLUMINATION FOR EASY VIEWING WITH 6 BEAKERS
d. SPEED (15 - 200)rpm
03-01-01608 | FURNACES : STUART SCIENTIFIC WITH SPARES FOR TWQ YEARS OPERATION | 2
* MAXIMUM TEMPERATURE = 1200C
* AUTOMATIC SWITCH OFF WHEN DOOR IS OPENED
* WEAR RESISTANT , DUST FREE , CERAMIC MUFFLE
* CHOISE OF TEMP. CONTROLLER
* ELECTRICAL SUPPLY 220-230V , 50Hz SINGLE PHASE , CURRENT RATING , HEATER POWER 1.5 KW
* CHAMBER DIMENSION 125x140.100mm
03-01-01609 | WATER STILLS (GFL) DOUBLE DISTILLATION 8 L/H MADE OF STAINLESS STEEL (220-230)V | 6
HEATING ELEMENT MADE OF STAINLESS STEEL WITH ALL ACCESSORIES WITH SPARES FOR TWO YEARS OPERATION
03-01-01610 | DIGITAL CONDUCTOMETER FOR CONDUCTIVITY MEASURMENT (MACHEREY - NAGEL MN) WITH AUTOMATIC TEMP. COMPENSATION FOUR MEASURING RANGES 0-20000 Ms/cm (PRECISION + 1%) | 3
PURE WATE CELL 2 POLES FO DISTILLED WATER FROM 0.1 TO 100 Ms/cm
* EMULSION CELL 2 POLES FOR DENSE SUBSTANCE 70 -200 Ms/cm
STANDARD SOLUTION FOR COND.
50Ms/cm sol , 500Ms/cm sol , 5000Ms/cm sol , 100Ms/cm sol ,
TEMPERATURE PROBES
* PRINTER 220 V
03-01-01611 | RUBBER VACUM HOSE | 2
THICK WALLED RUBBER HOSE FOR CONNECTING SUCTION FLASKS
AND VACUM PUMPS
03-01-01612 | CAPS FOR BIOLOGICAL CULTURE TUBE (SERO - TAP) MADE OF ANODISED ALUMINIUM WITH INTERNAL AISI 304 STAINLESS STEEL SPRING INSIDE THE CAP NOT BERMETICALLY SEALED , AUTOCLAVE AT 1 bar | 100
03-01-01613 | * CAPS FOR TABES Q= 24-26mm , COLOR GOLD AND SILVER | for each
03-01-01614 | * CAPS FOR TABES Q= 15-16mm , COLOR GANET AND BLUE | size
03-01-01615 | HAND VACUM PUMP WITH GAUGE (SARTORIUS) BODY OF PVC , SUPPLIED WITH GAUGE , VACUM RELEASE LEVER AND OF CLEAR PLASTIC CONNECTING TABING (50cm) . | 5
03-01-01616 | COLONY COUNTER (SARTORIUS) BATTRY OPERATED USED AS ABALL-POINT PEN , WITH FOUR DIGITAL LCD DISPLAY , SUPPLIED WITH MARKER REFILL . | 5
03-01-01617 | EM - DISPENSER WITH VOLUME (0-2)ml | 8
03-01-01618 | LAB. REFRIGERATOR | 3
TEMP. RANGE - 5 TO + 150C WITH METALLIC DOOR , DOUBLE GLASS ANTIMIST DOOR WITH SPARES FOR TWO YEARS OPERATION
03-01-01619 | SEMIAUTOMATIC SPECTROPHOTOMETER (UV & VIS) DOUBLE BEAM | 2
* WAVE LENGTH RANGE : 200 - 1000 nm
* BAND WIDTH : 2 nm
* ABSOR BANCE RANGE : 0.3 - 3.5 O.D.
* TRANSMITANCE : 0-100% T.
* LIGHT SOURCE : TUNGSTEN HALOGEN LAMP AND DEUTERIUM LAMP
* SAMPLE COMPARTEMENT : FOR 4 CUVETTES OF 10mm
* MIN SAMPLE VOLUME = 1ml
* MEMORY : 50 METHOD STORED
* POWER : 120 W , 220V , 50 Hz
ACCESSORIES ARE INCLUDED WITH THE INSTRUMENT :
* QUARTZ CUVETTES WITH LIDS. PATH LENGTH 10mm DIMENTIONS WITH SPARES FOR TWO YEARS OPERATION
* GLASS CUVETTES WITH LIDS , PATH LENGTH 10mm , INTERNAL DEPTH 10mm , EXTERNAL DIMENTIONS
* UV-2005 MANUAL
* TUNGSTEN HALOGEN And deuterium lamps
03-01-01620 | ATOMIC ABSORPTION SPECTROMETRY AMULTI ELEMENTS ANALYSIS ALL HEAVY METAL | 2
(Ag , Hg , Cr , Cd , As , Pb , Au , Ba , Co , Cu , Fe , Mn , Mo , Ni , Se , Ti , V , Zn , Na , K)
220 - 230 V
WITH ALL ACCESSORIES
* RECOMMENDED SPARES FOR TWO YEARS OPERATION
* SUPER LAMP POWER SUPPLY
* RECOMMENDED SPARES AND CONSUMABLE FOR TWO YEARS OPERATION
* FUME EXTRACTION SYSTEM
* COMPRESSOR
SETION 2-23: EQUIPMENTS FOR KARAMA & DOURA PROJECT
CODE | DESCRIPTION | QTY
03-01-01621 | ROTARY AIR BLOWER | 4
DELIVER RATE 3140 m/h DRY AIR
COMPRESSION 1300 m bar ABS
MOTOR 35 KW , 1480 rpm , 400 V , 50 Hz
IP - 44/F
03-01-01622 | AGITATOR FOR ALUM - TANKS | 6
WING DIAMETER 1000mm (MATERIAL SS)
LENGTH OF SHAFT 2600 mm
RATE OF CIRCULATION 6000 m3/h
GEAR MOTOR : 7 KW , 1400/125 rpm , 400V , 50 Hz
IP - 55 TROPICALIZED
03-01-01623 | 2 SPEED GEAR MOTOR (IMPELLER DRIVE) | 4
4 KW , 144/(1.6-8)rpm , 400V , 50 Hz
IP - 54/F
03-01-01624 | CABINET - MOUNTED CHLORINATORS | 12
CAPACITY 20Kg/h (1000 Lb/DAY)
03-01-01625 | WALL - MOUNTED CHLORINE GAS DETECTOR | 4
DETECTION LEVEL 1ppm VOL.
POWER SUPPLY 220V AC , 50 Hz
RELAY CONTACTS 1 N.O + 1 N.C 10A
SAMPLING RATE <= 0.1 m3/min
RESPONSE TIME <= 2 sec
WITH ACCESSORIES/3.0 m PVC AIR SAMPLE PIPE
WITH FITTING / INSECT SCREEN/GAS TESTING FITTINGS
03-01-01626 | TUBE OF PVC CEMENT , LIQUID CHEMECAL | 2
RESIDUAL CHLORINE ANALYZER
WALL - MOUNTED RESIDUAL CHLORINE ANALYZER
POWER SUPPLY 220V AC , 50 Hz
RELAY CONTACTS 1 N.O + 1 N.C FOR MIN & MAX
ALARM SETTING
INLET PRESSURE FOR DRINKING WATER 0.2 - 6 bar
OUT PUT SIGNAL 0 - 20 mA or 4 - 20 mA
SECTION 2-24: DUCTILE IRON PIPES DN 100,150,200 mm
CODE | DESCRIPTION | QTY
Supply of spigot-socket ductile iron pipes according to
ISO 2531 STANDARD, TYPE k9 with the following specifications:
1- pipes of push – fit joints.
2- lngth of pipe should be 6 meters
3- pipes should have spun – cement morter inside lining and outside bitumen coating.
SCOPE OF SUPPLY
SPUN DUCTILE IRON SPIGOT-SOCKET
03-01-01627 | 1- 100mm diameter pipe with rubber joint . | 100000LM
03-01-01628 | 2- 150 mm diameter pipe with rubber joint. | 50000LM
03-01-01629 | 3- 200 mm diameter pipe with rubber joint. | 25000LM
SUPPLY OF DUCTILE IRON FITTINGS
Fittings should be suitable for ductile iron pipes according to ISO 2531 STANDARDS with the following specifications.
1- Flanges should be of type NP16 .
2- All sockets joints should be mechanical
3- Fittings should have inside cement lining & outside b ituman coating.
4- The scope of supply include all necessry rubber joint ,gaskits,washers,bolts,nuts& washers.
SCOPE OF SUPPLY
03-01-01630 | 1- Flange socket 200 mm | 250 NO.
03-01-01631 | 2- Flange socket 150 mm | 500NO.
03-01-01632 | 3- Flange socket 100 mm | 1000NO.
03-01-01633 | 4- Flange spigote 200 m | 250NO.
03-01-01634 | 5- Flange spigote 150 m | 500NO.
03-01-01635 | 6- Flange spigote 100 mm | 1000NO.
03-01-01636 | 7- All socket tee 200 mm | 150NO.
03-01-01637 | 8- All socket tee , 200x150,150x100,(each) | 50NO.
03-01-01638 | 9- Double socket tee with flange branch 100x100 | 500NO.
03-01-01639 | 10- Double flange reducer 200x150mm,150x100,(each) | 250NO.
03-01-01640 | 11- Double flange reducer 150x100mm | 100NO.
03-01-01641 | 12- All socket tee 100x100 | 1000NO.
03-01-01642 | 13- All socket tee 150x150 | 500NO.
03-01-01643 | 14- Collar 100 mm | 1000NO.
03-01-01644 | 15- Collar 150 mm | 500NO.
03-01-01645 | 16- Collar 200 mm | 250NO.
03-01-01646 | 17- Double socket bend 45,90 deg.(each),100mm | 1000NO.
03-01-01647 | 18- Double socket bend 45,90 deg.(each),150mm | 500NO.
03-01-01648 | 19- Double socket bend 45,90 deg.(each),200mm | 250NO.
03-01-01649 | 17- Double socket bend 22 1 /2, 11 1 /4 (each) 100mm | 500NO.
03-01-01650 | 18- Double socket bend 22 1 /2, 11 1 /4 (each) 150mm | 150NO.
03-01-01651 | 19- Double socket bend 22 1 /2, 11 1 /4 (each) 200mm | 50NO.C62
General specifications
1- Thickness of pipe according to formula
e= 5.8 + 0.003xDN
2- Internal pressure proof test = 50 bars
3- Thickness of fitting according to formula
e= 7+0.014xDN, for Tees, k=14
e= 6+0.012xDN, for other fittings , k=12
4- Leak tieghtness test for fitting = 25 bars
5- Thickness of lining = 2.5 mm
SECTION 2-25: Supply of upvc Fittings
CODE | DESCRIPTION | QTY(NO.)
Supply of fittings for UPVC pipes according to DIN 8061 & 8062 .(class 10 bars) with the following specifications,
1- Fittings should be manufactured from cast iron with epoxy piant enternally and externally .
2- Flanges should be of type NP16.
3- The scope of supply including all necessary rubber joint,washers, bolts,nuts,gaskits.
Scope of supply
03-01-01652 | 1- All socket tee, 110mmx110 mm | 1000
03-01-01653 | 2- All socket tee, 160mmx110 mm | 500
03-01-01654 | 3- All socket tee, 160mmx160 mm | 250
03-01-01655 | 4- All socket tee, 225mmx160 mm | 150
03-01-01656 | 5- All socket tee, 225mmx225 mm | 100
03-01-01657 | 6-Double socket bend 90◦, 110mm | 500
03-01-01658 | 7- Double socket bend 90◦, 160mm | 300
03-01-01659 | 8- Double socket bend 90◦, 225mm | 100
03-01-01660 | 9- Double socket bend 45◦, 110mm,160mm (each) | 150
03-01-01661 | 10- Double socket bend 45◦, 225mm | 50
03-01-01662 | 11-Flange spigot & flange socket 110 mm each | 200
03-01-01663 | 12- Flange spigot & flange socket 160 mm each | 150
03-01-01664 | 13- Flange spigot & flange socket 225 mm each | 150
Supply of valves
Specifications:
1- Valve should be of rubber disc seal type.
2- Flange should be PN16 type .
3- Testing pressure should be 18 bars against seal and 25 bar against body.
4- Ccoating should be of epoxy paint enternally & externally .
5- All coating should be of feed stuff quality.
Scope of supply
03-01-01665 | 1- Double spigot valve 110 mm | 500
03-01-01666 | 2- Double spigot valve 160 mm | 250
03-01-01667 | 3- Double spigot valve 225 mm | 100
SECTION 2-26: FERRULES MOUNTED ON SADDEL FOR HDPE PIPE AND STEEL CLAMPS
SCOPE OF SUPPLY
03-01-01668 | 1-COMPLET SET OF 110MM SADDEL WITH 12MMX12MM FERRULE. | SET | 60000
03-01-01669 | 2- = = = = = 25MMX25MM = . | SET | 2000
03-01-01670 | 3- = = = = = 18MMX18MM = | SET | 5000
03-01-01671 | 4- = = 160MM = = 12MMX12MM = | SET | 10000
03-01-01672 | 5- = = = = = 18MMX18MM = | SET | 3000
03-01-01673 | 6- = = = = = 25MMX25MM = | SET | 3000
03-01-01674 | 7- = = 225MM = = 12MMX12MM =. | SET | 5000
03-01-01675 | 8- = = = = = 25MMX25MM =. | SET | 1000
03-01-01676 | STAINLESS STEEL REPAIR CLAMP TYPE RS-1, RANGE MM( 115-125) | NO. | 7000
03-01-01677 | STAINLESS STEEL REPAIR CLAMP TYPE RS-1, RANGE MM(112-121) | NO. | 3000
03-01-01678 | STAINLESS STEEL REPAIR CLAMP TYPE RS-1, RANGE MM(166-178) | NO. | 2000
03-01-01679 | STAINLESS STEEL REPAIR CLAMP TYPE RS-1, RANGE MM(178-190) | NO. | 5000
03-01-01680 | STAINLESS STEEL REPAIR CLAMP TYPE RS-1, RANGE MM(215-227) | NO. | 1000
03-01-01681 | STAINLESS STEEL REPAIR CLAMP TYPE RS-1, RANGE MM(233-246) | NO. | 3000
03-01-01682 | STAINLESS STEEL REPAIR CLAMP TYPE RS-1, RANGE MM(271-293) | NO. | 1000
03-01-01683 | STAINLESS STEEL REPAIR CLAMP TYPE RS-1, RANGE MM(346-368) | NO. | 800
03-01-01684 | STAINLESS STEEL REPAIR CLAMP TYPE RS-1, RANGE MM(369-392) | NO. | 200
KARAMA & DOURA PROJECT
CODE | DESCRIPTION | QTY
03-01-01685 | ROTARY AIR BLOWER | 4
DELIVER RATE 3140 m/h DRY AIR
COMPRESSION 1300 m bar ABS
MOTOR 35 KW , 1480 rpm , 400 V , 50 Hz
IP - 44/F
03-01-01686 | AGITATOR FOR ALUM - TANKS | 6
WING DIAMETER 1000mm (MATERIAL SS)
LENGTH OF SHAFT 2600 mm
RATE OF CIRCULATION 6000 m3/h
GEAR MOTOR : 7 KW , 1400/125 rpm , 400V , 50 Hz
IP - 55 TROPICALIZED
03-01-01687 | 2 SPEED GEAR MOTOR (IMPELLER DRIVE) | 4
4 KW , 144/(1.6-8)rpm , 400V , 50 Hz
IP - 54/F
03-01-01688 | CABINET - MOUNTED CHLORINATORS | 12
CAPACITY 20Kg/h (1000 Lb/DAY)
03-01-01689 | WALL - MOUNTED CHLORINE GAS DETECTOR | 4
DETECTION LEVEL 1ppm VOL.
POWER SUPPLY 220V AC , 50 Hz
RELAY CONTACTS 1 N.O + 1 N.C 10A
SAMPLING RATE <= 0.1 m3/min
RESPONSE TIME <= 2 sec
WITH ACCESSORIES/3.0 m PVC AIR SAMPLE PIPE
WITH FITTING / INSECT SCREEN/GAS TESTING FITTINGS
03-01-01690 | TUBE OF PVC CEMENT , LIQUID CHEMECAL | 2
RESIDUAL CHLORINE ANALYZER
WALL - MOUNTED RESIDUAL CHLORINE ANALYZER
POWER SUPPLY 220V AC , 50 Hz
RELAY CONTACTS 1 N.O + 1 N.C FOR MIN & MAX
ALARM SETTING
INLET PRESSURE FOR DRINKING WATER 0.2 - 6 bar
OUT PUT SIGNAL 0 - 20 mA or 4 - 20 mA