## XII 02-06
02-06-00598 | air handlig unit for operating theater room
|  | type / wiss technick | [7 empty] | 100A.H.U
capasity = 50ton
heating = heater for (A and B)
A - HP = 3/10.5
flow = 2500 / 4250M^3/hr
B - HP = 1.5/5.5
| flow = 1500/ 3250 M^3/hr | [8 empty] | 100AHU
R.P.M for A and B = 1500/ 3000
NO. of ROW for (A and B)=3
three type of filter for (A and B)
a -bag filter (washable
b -mesh typy (washable) G.S
C- absolute filter 99.9%
volt = 380 V/ 3 PH / 50HZ
02-06-00599 | A .H. U
| ctm=14800ctm | [8 empty] | 100
HP= 8.5HP
heating=hot water
RPM= 1500/ 3000
volt = 380V / /50HZ
feltr = mesh tepe (washable)(G.S)
A .H. U
| HP | V | QTY | flow M^3/hr | type of filter
02-06-00600 | 2 | 380/3ph/50hz | 100 | 31 50 | mesh type (washable)
02-06-00601 | 7.5 | 380/3ph/50hz | 100 | 8160 | mesh type (washable)
02-06-00602 | 7.5 | 380/3ph/50hz | 100 | 9960 | mesh type (washable)
02-06-00603 | 7.5 | 380/3ph/50hz | 100 | 7990
02-06-00604 | 7.5 | 380/3ph/50hz | 100 | 8560
02-06-00605 | 3.o | 380/3ph/50hz | 100 | 3080
02-06-00606 | 7.5 | 380/3ph/50hz | 100 | 3080
02-06-00607 | 10 | 380/3ph/50hz | 100 | 7250
02-06-00608 | 7.5 | 380/3ph/50hz | 100 | 4000
02-06-00609 | 7.5 | 380/3ph/50hz | 100 | 4000
02-06-00610 | 20 | 380/3ph/50hz | 100 | 16190 | mesh type (G.S)
02-06-00611 | 7.5 | 380/3ph/50hz | 100 | 6800 | mesh type (G.S)
02-06-00612 | 7.5 | 380/3ph/50hz | 100 | 4400 | mesh type (G.S)
02-06-00613 | 40 | 380/3ph/50hz | 100 | 31700 | mesh type (G.S)
02-06-00614 | 30 | 380/3ph/50hz | 100 | 31005 | mesh type (G.S)
02-06-00615 | 25 | 380/3ph/50hz | 100 | 33030 | mesh type (G.S)
02-06-00616 | 15 | 380/3ph/50hz | 100 | 19500 | mesh type (G.S)
heating = hot water
RPM = 1500 - 3000
NO.of row = 3
02-06-00617 | FIER ALARM SYSTEM
a)specification :
1- the system should be 2- wire installation
2- the system should be able to be connected to data network or telephone exchange and recorder
3- the system should contain repeaters for stopping air condtioning and spare
4- each zone contain about 20 delectors and one glass break unit
5- the system should contain one central control and indication unit and branchs units
6- each system contain PC unit for operation and maintenance and programing if necessory
7- the detecters should be from smoke heat and temp rise type
b) quantities :
| no. of system | [8 empty] | no. of zone
| 500 | [8 empty] | 10
| 500 | [8 empty] | 20
| 500 | [8 empty] | 30
| 500 | [8 empty] | 40
| 500 | [8 empty] | 60
| 500 | [8 empty] | 80
| 500 | [8 empty] | 120
c)
1- one year warrenty from date of operation and tow years maintenece after period of warrenty
2- spare partes for 5- years
3- full sets of ducomants and catalogues and diagrams
4- training on factory of equipment and local training during installation
MEURO - SURGERY CENTER
LUNDRY EQUIPMENT
02-06-00618 | side loading washer 50 kg | [8 empty] | 200
02-06-00619 | centrefugal extractor 30 kg/load | [8 empty] | 200
02-06-00620 | drying tembler 25 kg/load | [8 empty] | 200
02-06-00621 | canvas truck | [8 empty] | 200
02-06-00622 | strach cooker | [8 empty] | 200
02-06-00623 | flate work ironer 50 kg/hr | [8 empty] | 200
02-06-00624 | hand ironer board | [8 empty] | 200
02-06-00625 | swing machine | [8 empty] | 200
02-06-00626 | ottlity press machine | [8 empty] | 200
02-06-00627 | kerosen steam boiler 20 BHP capac. At apressure of 11kg/cm2 | [8 empty] | 200
a- general fire tupe steam boiler
1-package , automatic factory assembled , on steel base piped , wired , tested and ready for connec - tion to water , fuel and powersupply 11 bar
2- desing working pressure
3-controls and circuits grounded and to operate on 240 volts 50 hz
4-suitable for firing with fuel oil np.2
5-over all efficiency not less than 80%
6-certified test resolts to be submitted
7-operation , maintenance , repair and spare parts manuals to be submitted
b-capacity: 500 kg of steam /hr
c- design: the boiler shall be of horizontal fire tube type , equiped with the following:-
1- shell to be designed , constructed , and hydro-statically , tested in accordance with ASME boiler and pressure vessel code
_ to be equiped with sufficient manholes handholes lifting eyes, heavy steel base target rin for flame reshaping & means of constant contrrol flow of water
2-front &rear doors to be gantight &rexplosion proof and suitable for inspecting tube sheets &flues
3- re - fractories to be of high quality , high tem - perature material laid in high temp cement
4-flame observation parts with pyrex glass and steel cover
5-insulation and jacket to be 50mm fider glass insulation unler sectional prefer 1mm (20 gauge) g . I . Sheet met lagging . A suitable cat walk to be equiped to the boiler
6-painting to be heat resistant enamel
d- accessories to include:-
1-flanged inlet with isolating valve
2-flanged out let with isolating valve
3-flanged relief valve
4-screwed press , gauge 200mm
5-screwed thermometers
6-drain valves , y type
7-high steam press limit control
8-water column ass including gauge glass , try cocks , low water cut - off and feed pump control with alarm contacts
9-blow down uessel and valve
10-feed water pump of a capacity and head sutibale for boiler capacity
11- second high limit switch
12-second low water cut off
13-hand injector for feed pump
14-feed water system
e-control circuit to slut off fuel supply in the event of
1-low water level
2-forced draft fan failure
3-ignition failure
4-main flamo failure
5-low oil press
f-burners to be fully automatic pressure atomising nossle forced drought type designed to fire fuel no. 2 or L.P.G each burner to be equiped with the following:
1-relays for prepurging & post p.u.r. gina oil burner nozzles
2-ienition transformer & electronics
3-rotary fuel oil pump with manual change over switch
4-bloower with automatic starter
5-oil strainer , valves , check valves & solenois valve
6-oil pressure regulating valves
7-oil pressure gauge
8-flame failure deteector
9-external mix gas burner
10-gas - electric ignition
11-air flow safety awitch
12-main gas : train consisting oe gas volume control valve , manual gas cock and automatic diaphram gas valve
g- condensate return system equiped with
1- receiver tank with acapacity not less than 5 - times the amount of condensatc perminute
2-condensate pump with a capacity not less than 2.5 times normal flow
3-adjustable float switch and gauge glass to be fitted to the receiver tank
h- chimney and insulation :-to be supplied made of black steel gauge 14 welded thru out reinforced and braced with angle iron members to be fitted with removable clean out plates barometric damper for maintaining correct draft
the clrimney shall be insulated with matac lath 85% magnesia 150 mm insulation the chimney to be coated with plastic smok pipe covering to reduce condensation a breaching with suitable clean out to be supplied for connecting boiler to vertical stack
I- softener : iron exchange softener of a capacity suitable for boiler capacity complete with brine tank and all other accessories required the feed water hardness 700 ppm
nos of boiler required 20 set with all other mentioned accessories above
02-06-00628 | air compressor with cylinder 0.07 m3/min capac. At apressure of 6 kg/cm2 cylinder rolame 120 l | [8 empty] | 200
02-06-00629 | disinfected washing machine | [8 empty] | 200
| ELECTRICAL EQUIPMENT | [8 empty] | 200
02-06-00630 | high tension panal with short circuit current (25 ka)
02-06-00631 | high tension cable , XLPE type with (750) m length | [8 empty] | 40
02-06-00632 | isolated transformer | [8 empty] | 6x150mm2
| with their control panales | [8 empty] | 50
capacity (25 kva)
| capacity (16 kva) | [8 empty] | 50
| KITCHEN EQUIPMENT | [8 empty] | 50
02-06-00633 | scale 1 kg
02-06-00634 | scale 25kg | [8 empty] | 500
02-06-00635 | scale 5 kg | [8 empty] | 500
02-06-00636 | weighing machine 100 kg | [8 empty] | 500
02-06-00637 | potata peeler 5kg /load | [8 empty] | 500
02-06-00638 | vegetable mill 300 kg /hr | [8 empty] | 500
02-06-00639 | chopping black 50x50x65 cm | [8 empty] | 500
02-06-00640 | meat mincer 2 kg /hr | [8 empty] | 500
02-06-00641 | backing oven gaseous loven 2 deck each 80x90x120cm | [8 empty] | 500
02-06-00642 | mixing machine 10 lit | [8 empty] | 500
02-06-00643 | refrigerator 420 lit | [8 empty] | 500
02-06-00644 | range gaseous (general purpose) 6 plate - 1oven | [8 empty] | 500
02-06-00645 | oven gaseous (each one of 80x90x170 cm) | [8 empty] | 500
02-06-00646 | boiling pan gaseous 35 lit | [8 empty] | 500
02-06-00647 | boiling pan gaseous 50 lit | [8 empty] | 500
02-06-00648 | gaseous fry range | [8 empty] | 500
02-06-00649 | grill gaseous | [8 empty] | 500
02-06-00650 | hot cub board | [8 empty] | 500
02-06-00651 | dish washer 640 pieces/hr | [8 empty] | 500
02-06-00652 | heated trolly | [8 empty] | 500
02-06-00653 | general purpose trolly | [8 empty] | 500
02-06-00654 | cold cup board | [8 empty] | 500
02-06-00655 | electrical water cooler 40 lit/hr | [8 empty] | 500
02-06-00656 | hood | [8 empty] | 500
02-06-00657 | bin on castors 6 kg | [8 empty] | 500
02-06-00658 | bin on castors 12.5 kg | [8 empty] | 500
02-06-00659 | bin on castors 25 kg | [8 empty] | 500
02-06-00660 | bin on castors 50 kg | [8 empty] | 500
VIDEO BEAMER
02-06-00661 | large avitoriom high lumihosity for use in light remote controlled ,complete system with link to speakers computer and monitor to accept CD rom as well | [8 empty] | 100
02-06-00662 | slide progector | [8 empty] | 200
02-06-00663 | over head projector | [8 empty] | 500
02-06-00664 | cooling tower schedule
| no req. | type | heat rejection capacity kcal/h | ambint W.B temp. C | water temp. |  | water qty. L/min | fan | electrical characteristics
[5 empty] | In | Out |  | motor kw | V | PH | HZ
| 200 | indused draft | 869400 | 26 | 35 | 30 | 2611 | 15 | 380 | 3 | 50
02-06-00665 | air washer schedual
| no. req | type | location | summer |  |  | winter (heating coil) | [9 empty] | blower |  |  |  |  | circulation water pump kw | electrical characteristic |  |  | filter
|  |  |  | amb. Temp wb c | press. Nozzle m.w.g | water circulation lit/min | grand total heat kcal/hr | air temp c |  |  |  | water temp.c |  | water qty lit/min | no of fins /25mm | no of rows | blower type | total air qty m/hr | face velocity m3/sec | total static pressure mm w g | motor kw |  | volt | phase | hertz | type | thickness mm
[8 empty] | in |  | out |  | in | out
[8 empty] | DB | WB | DB | WB
| 200 | double bank spray | block c on the roof | 26 | 25 | 750 | 431680 | 1.5 | 0.8 | 33.5 | 5.5 | 82 | 71 | 650 | 8 | 2 | centrifugal aerofoil | 121380 | 2.5 | 22 | 18 | 7.5 | 380 | 3 | 50 | metalic cleanable | 50
extractor fan
| RE NO. | location | air capacity m3/hr | no. req | pressure drop mm.w.h | input kw | electric v/ph/hz
02-06-00666 | RE-16 | A" | 1460 | 100 | 4 | 0.12 | 220/1/50
02-06-00667 | RE-17 | B | 1300 | 100 | 3 | 0.065 | 220/1/50
02-06-00668 | RE-18 | B | 12000 | 100 | 10 | 1 | 380/3/50
02-06-00669 | RE-19 | B | 3400 | 100 | 7 | 0.3 | 220/1/50
02-06-00670 | RE-20 | B | 2210 | 100 | 7 | 0.3 | 220/1/50
02-06-00671 | RE-21 | B | 1530 | 100 | 5 | 0.2 | 220/1/50
02-06-00672 | RE-22 | B | 1020 | 100 | 5 | 0.2 | 220/1/50
02-06-00673 | RE-23 | A` | 2430 | 100 | 5 | 0.5 | 220/1/50
02-06-00674 | RE-24 | A" | 1785 | 100 | 5 | 0.5 | 220/1/50
02-06-00675 | RE-25 | A" | 3100 | 100 | 5 | 0.75 | 220/1/50
02-06-00676 | RE-26 | A" | 340 | 100 | 3 | 0.3 | 220/1/50
02-06-00677 | RE-27 | A" | 1445 | 100 | 5 | 0.5 | 220/1/50
02-06-00678 | RE-28 | A" | 3215 | 100 | 5 | 0.5 | 220/1/50
02-06-00679 | RE-29 | A" | 2516 | 100 | 5 | 0.5 | 220/1/50
02-06-00680 | RE-30 | A" | 1600 | 100 | 3 | 0.3 | 220/1/50
02-06-00681 | RE-31 | A" | 1900 | 100 | 3 | 0.5 | 220/1/50
02-06-00682 | RE-32 | A" | 2265 | 100 | 3 | 0.5 | 220/1/50
02-06-00683 | RE-33 | A" | 1700 | 100 | 3 | 0.5 | 220/1/50
02-06-00684 | RE-34 | A | 1657 | 100 | 3 | 0.3 | 220/1/50
02-06-00685 | RE-35 | A`,A` | 1000 | 100 | 3 | 0.3 | 220/1/50
02-06-00686 | hood
| stainlees steel hood used for labortary to be installed above sterilizer with following dimension 1500x600 | [8 empty] | 100
02-06-00687 | water cooler | [8 empty] | 500
40 l/h cooled to 10 c
electric supply 220/1 ph/50
stainlees steel ,anti-splash top equipped with non-clogging and easy to clean integral stranier grid the tank shall be burst proof galvanized with copper refrigerator coil
02-06-00688 | window type 2 ton with heater capacity 3.6 kw | [8 empty] | 100
02-06-00689 | window type 1.5 ton with heater capacity 3 kw | [8 empty] | 100
02-06-00690 | window type 1 ton with heater capacity 2.6 kw | [8 empty] | 100
02-06-00691 | split unit 2 ton with heater capacity 3.6 kw | [8 empty] | 100
02-06-00692 | x-ray window 1.5x1.2m w/load glass | [8 empty] | 100
02-06-00693 | x-ray door fram 1.8x2.35 m w/load sheilding | [8 empty] | 100
02-06-00694 | x-ray door fram 0.9x2.1 m w/load sheilding | [8 empty] | 100
02-06-00695 | drinking water storge tank made of hot pressed steel plate of dimension (1.22x1.22) and thickness of not less than 6mm
| (7.32x4.88x2.44) m | [8 empty] | 100
| (4.88x2.44x2.44)m | [8 empty] | 100
02-06-00696 | inclarator of 300 kg /hr | [8 empty] | 100
02-06-00697 | BED HADE UINT | [8 empty] | 100UINT
each one of bed hade unit comprifing the following
| * general light 40 w with lamp | [8 empty] | 100
| * read light 20 w with lamp | [8 empty] | 100
| *cord pull switch with lamp for nurse call station | [8 empty] | 100
` | * intercom unit | [8 empty] | 100
| * doubl switch socket 13A | [8 empty] | 100
| *exam light with lamp | [8 empty] | 100
| *extra examenstion light with lamp shipt 44 seperatly | [8 empty] | 200
02-06-00698 | cold room | [8 empty] | 100
temp.: -20C to +20 C
dimention (H 2.5 m- W3 m- L3m)
cold room 2 stage unites
02-06-00699 | santiry hot water with hot pump
| power 3kw , rev 1450 sec , suction 79 mm, discharge 64mm, capacity 14 l/min , head 30m | [8 empty] | 100
02-06-00700 | SPECIFICATIONS FOR TANK TRUCK | [8 empty] | 1000
( GAS OIL - CESSPOOL EMPTIER DRINKING WATER)
1) Truck Specification
1- Type : Forward control
2- Drive sys. 4 X 2
3- Loading Cap. (10.000 liters Gas oil)
( 8.000 liters cesspool emptier)
(10.000 liters drinking water)
4- Dimensions
Wheel base about 4.100 mm
Overall length about 7.535 mm
Overall width about 2.480 mm
5- Engine : Diesel engine water cooled
6- Electrical eq. : 24 Volt, 12 volt X2 Batteries, 120 Ah at 20 hr
7- Transmission : Manual Power assist
8- Clutch : Hydraulic control, single dry plate with air pressure assistance.
9- Tires : Single Front, dual rear
10- Steering : Left hand steering, Ball mute type with integral type hydraulic power booster, Telescopic and tilt steering column with steering lock.
11- Front suspensions: Laminated leaf springs with shock absorbers
12- Rear Suspensions : Laminated leaf springs
13- Front : Parallel, Tapered channel section type with cross - member and reinforcements
14- Fuel Tank : 250 liters
15- Drivers Cab : All steel, tilt cab equipped with A/C
16- Paint : Finish coat, Crystal white
17- Measurement : Metric ( Km/h)
18- Caution Plate : Arabic
19- Brakes :
Service : Air over hydraulic with dval circuit
Parking : internal expanding type on propeller shift
Auxiliary : Exhaust brake
20- Cooling system :
Radiator : corrugated fin type with pressure cap and surge tank
Fan : Multi – blades, steel
2) TANKS : Specifications
A – Gas Oil Tank
* Capacity: 10.0 KL. Gas Oil
* Type : Elliptical cross sectioned cylindrical tank
* Tank construction: tank assembly of elliptical shape, constructed with steel plate by electric welding which consists of tank shell, end plate, apparition plate, of lashing and manholes (inside 400mm dia.) each manhole cover is furnished with a filling hatch (inside 230mm Dai.) a dip stick, an air vent valve and a filling point interior surface of tank is zinc painted anti- corrosion.
* Loading and emptying : emptying by pumping or gravity pump capacity 600 liters/min at 600 r.p.m
* Attachments :
| a- Hose locker |  |  |  | Two, both sides of tank shell
| b- Ladder |  |  |  | One, at left side in rear of tank
| c- Tool box |  |  |  | One, mounted on frame
| d- Bumper |  |  |  | One ,rear end of chassis frame
| e- Fire extinguish |  |  |  | Two, both side of vehicle
| f- Earth reel |  |  |  | One, at left side of vehicle
| g- Earth chain |  |  |  | One, at rear of vehicle
| h- Muffler with spark arrested |  |  |  | One, provided at front side of vehicle
* Accessories :
| a- Hose (for suction or delivery) 63mm X 3mm | [8 empty] | 2 PCS
| b- Hose wrench | [8 empty] | 2 PCS
* Dip stick is Marked on every 1000 liters
B- Cesspool Emptier Tank
* Cap : 8000 Liters
* Type : Elliptical cross sectioned cylindrical tank
* Tank construction : Tank assembly is elliptical shape, and constructed with steel plate by electric welding it consists of tank sheu, and plates, a main manhole, peep holes, 2-way ball valves and blind manholes. Interior surface of tank is zinc painted for anti- corrosion.
* Loading and emptying : By vacuum pump ( by increasing or decreasing tank pressure).
Pump capacity : 2.790 lit/min at 500 r.p.m
* Equipment :
| a- Delivery hose |  |  |  | 75mm dia x 6m |  |  |  |  | 1 PC
| b- Suction hose |  |  |  | 65 dia x 10m |  |  |  |  | 1 PC
| c- Tool box |  |  |  | one mounted on frame
* Color : Finish coat, crystal white
C – (Drinking Water Tank)
* Capacity : 10.0 KL Drinking water
* Type : Elliptical cross sectioned cylindrical tank
* Tank construction : tank assembly of Elliptical shape, constructed with stainless plate by electric welding which consists of all its part.
And the tank has the parts and equipment that is necessary in the use and carrying the drinking water
* Loading and emptying:
Loading by pumping and by normal feeding from upper manhole
Emptying : by pumping and by gravity
02-06-00701 | over head projection | [8 empty] | 100
02-06-00702 | slide projection | [8 empty] | 100
02-06-00703 | flower making machine | [8 empty] | 100
flower making machine with spaer parts warranty 2 years maintenance two years capacity one ton per hours (1000kG/HR)
02-06-00704 | grain crushing mashine mashine | [8 empty] | 100
grain crushing mashine mashine with four different pore size sleeve capacity one ton per hour (1000KG/HR)
02-06-00705 | mixer | [8 empty] | 100
mixer capacity (1000 KG/HR)
02-06-00706 | oven | [8 empty] | 100
oven with fan- hot air for drying animal food medium size
02-06-00707 | pasute making machine | [8 empty] | 100
pasute making machine capacite 100 KG/HR
02-06-00708 | hot water boiler 2.5 ton /hr | [8 empty] | 100
02-06-00709 | sealed-acid battery 70A/H/long life | [8 empty] | 2000
02-06-00710 | sealed-acid battery 135A/H-long life | [8 empty] | 50000
02-06-00711 | sealed-acid battery 200A/H-long life | [8 empty] | 2000
02-06-00712 | Ni-cd-battery 6A/H 6V | [8 empty] | 1000
Targeted Nutrition Programme
02-06-00713 | field vehicle Transportion of supplies and Monitoring / supervision of the programme 200 (2 cars / district + 26 for govermorat and central levels ) | [8 empty] | 1000 each
02-06-00714 | Computer (1 per grovermorat , 2 of Baghdad and 4 for NRI) to improve CCCU/PHC database | [8 empty] | 1000 each
02-06-00715 | Fork lift 3 ton ( to be used storage places at Govermorate for high protein biscut and therapeutic milk) | [8 empty] | 1000 each
02-06-00716 | Motorcycle (one for each PHC center for monitoring at field level ) | [8 empty] | 3000 each
02-06-00717 | electric cooking heater (for use at PHCs) | [8 empty] | 10000 each
02-06-00718 | ceiling fans (for use at PHCs/CCCUs) | [8 empty] | 10000 each
North of Iraq / health
02-06-00719 | Water tank trunk 8-10000 liter capacity , LHD with Export Specs for Iraq & manuf. Recommended spare for 2 yrs. Operation | [8 empty] | 2
02-06-00720 | equipment :Oxygen factory | [8 empty] | 100
1-type (10X-100)
2-production capacity 100 liter/hour
3-purity99.5-99.9%
4-voltage 380V
5-current 600-100A
6-oxygen container of 22000 liter with
a- oxygen gas pump
b-charging desk
02-06-00721 | freeze dryes | [8 empty] | 100
malti shell
shell area 5m^2
temp range -50 _ +70
vacum pump 10m^3/hr 220 _ 240V
02-06-00722 | deep freezer | [8 empty] | 100
stainless steel intesior
capacity 200 _ 250 liters
miuoprocessor control
digital display
tempretare -220 _ -85C 220 _ 240V
02-06-00723 | vacum packiging + sealing | [8 empty] | 100
machine 220 - 240V
02-06-00724 | laminas flow cabinet | [8 empty] | 100
with bench _ speed control
rate 100 fpm 220 _ 240V
02-06-00725 | analytical balance | [8 empty] | 100
weishing capasity 205gm 220 _ 240V
02-06-00726 | drying / sterilization cabin | [8 empty] | 100
(bio haz and # biological
UV light 220 _ 240v
02-06-00727 | A W U.(air washer unit) | [8 empty] | 100
tupe 2 bank conter flow type centerfugul single suction fan
fan section :-back ward 2nclined blade
sizedia.:- 750mm
width 188mm
no V-belt :-3
jupply air volume 25900 cmH X 106MMAQ
retunn air volume OCMH,out door air volume 25900 CMH
motor 15KW , 3Q , 380V , 50HZ heatring coil
air section :capacity :- 144000 KCAr/H
watir flow rate 200L/min
water temp (in-out) 83c/71c
air temp:-(in-out) (-1.0-15.0)
rows & fin ptch 2rows x 2.9mm hatinial copper tube aluminin
filter ass.:- NBS 35%
02-06-00728 | . Tyres and Tubes Required For Health Institutions in Iraq
| 600 x 14 | [8 empty] | 1500
| 650 x 14 | [8 empty] | 1500
| 700 x 15 | [8 empty] | 2000
| 750 x 16 | [8 empty] | 1500
| 205 x 16 | [8 empty] | 1500
| 650 x 16 | [8 empty] | 1000
| 1200x 20 | [8 empty] | 1000
| 1100x 20 | [8 empty] | 1000
| 1200x 24 | [8 empty] | 500
| 1000x 20 | [8 empty] | 250
02-06-00729 | computer
| computer network to cover pentium 111 with acc:malti media | [8 empty] | 100
| digital camera | [8 empty] | 100
| P.C viewer | [8 empty] | 100
| scanner | [8 empty] | 100
| colour printer | [8 empty] | 100
| printer-laser jet | [8 empty] | 100
| portable screen | [8 empty] | 100
| C.D read-write | [8 empty] | 100
| C.D row | [8 empty] | 5000
| flophy disc | [8 empty] | 10000
| video blaster with cammera | [8 empty] | 100
| modem | [8 empty] | 100
02-06-00730 | battery charger
| typ |  | capacity |  | power KW | charging current | out put voltage | in put voltage |  | qty
| cadmium Qsc50-86 |  | 50AH/5HR |  | 2.1KW | 15A | E130-DCV | 380V |  | 100
| QE200E-20 |  | 200AH/HR |  | 1.36KW | 40A | F27-DCV | 380V |  | 100
| QE200E-20 |  | 200AH/HR |  | 1.36KW | 40A | E29.4-DCV | 380V |  | 100
| Qfw600E-20 |  | 600AH/HR |  | 3.4KW | 100A | F27-DCV | 380V |  | 100
| QKC80E-40 |  | 80AH/5HR |  | 1.92KW | 13. 75 | F56.8DCV | 220V |  | 100
| QKC80E-40 |  | 80AH/5HR |  | 1.92KW | 13. 75 | E60.8DCV | 220V |  | 100
02-06-00731 | Mobile lab. For air pollution monitoring (sampling and analysis system)containing ( high volume sampler for measuring total suspended particulates (T.S.P.) , carbon monoxide (CO)analyzer ,Sulfur Oxides (SOx)analyzer ,Total hydrocarbon (THC)analyzer, ozone (o3) analyzer, hydrogen sulfide (H2S analyzer) with standard calibration gases for the above analyzers instuments for measuring the meteorological parameters (wind speed & direction , temp, and humidity) in addition to especially programmed computer and calibration unit and data handling unit for the above instruments and electrical power generator | [8 empty] | 100
02-06-00732 | Mobile water lab. Carried by a car containing ( pH meter , turbidometer, portable spectrophotometer & spectrophotometer with U.V lamp , dissolved oxygen meter, COD reactor , TOC analyzer, deionizer , distillator , refrigerator , electrical generator | [8 empty] | 100
02-06-00733 | Mobile lab. for monitoring Environmental Background Radiation with all accessories containing : | [8 empty] | 100
02-06-00734 | Sodium iodide crystal with multichemical analyzer | [8 empty] | 100
02-06-00735 | Portable dust samplers | [8 empty] | 100
02-06-00736 | Portable dose (dose- rate) meter | [8 empty] | 100
02-06-00737 | automatic developing and fixing system for processing personal films | [8 empty] | 100
02-06-00738 | Accessories for Rotork analysis model 400 - CO analyzer (Rotork co ) :-
02-06-00739 | Mannual for model 400dual been infrared analyzer | [8 empty] | 100
02-06-00740 | Calibration gas cylinder ( 50 ppm ) | [8 empty] | 100
02-06-00741 | boat for river survay ( 8 horse , using benzene as fule capacity 7 persons | [8 empty] | 100
02-06-00742 | power supply
| V in-pot |  | V out-pot |  | AM | KW | capaste battrey |  |  | QTY
| 24V DC |  | 380V DC |  | 30A | 15KW | 182*2 |  |  | 100
02-06-00743 | Passengers intercity staff bus .40 to 50 passengers,automatic doors ,diesel engine,air condtioned,apholestered chairs stainless steele fram,sliding glass windows with curtains,rubber mat floor, tinted windshield , stereo radio-recorder,ceiling hanging grips, | [8 empty] | 1000
AXIAL AEROFOIL AND PROPELLER EXHUST FAN
| fan NO. | block location | TYPE | capacity m3/hr | no. req | external static pressure m.w.a | input kw |  | electric characterishi
02-06-00744 | R.F16 | B | axial aerofoil with motor inside case. | 14000 | 100 | 10 | 4 |  | 380/3/50
02-06-00745 | R.F17 | A | axial aerofoil with motor inside case. | 5950 | 10 | 5 | 2.5 |  | 380/3/50
02-06-00746 | R.F18 | A | axial aerofoil | 4180 | 10 | 7 | 2.5 |  | 380/3/50
02-06-00747 | RF.19 | A | axial aerofoil | 5830 | 10 | 10 | 3 |  | 380/3/50
02-06-00748 | RF.20 | A | axial aerofoil | 2870 | 10 | 10 | 1.5 |  | 380/3/50
02-06-00749 | RF.21 | A | axial aerofoil | 4280 | 10 | 6 | 1.5 |  | 380/3/50
02-06-00750 | RF.22 | A | axial aerofoil | 2500 | 10 | 7 | 1 |  | 380/3/50
02-06-00751 | RF.23 | A | axial aerofoil | 5000 | 10 | 7 | 3 |  | 380/3/50
02-06-00752 | EX.6 | A"-ground | axial wall mounted | 1200 | 10 | 5 | 0.3 |  | 1/220/50
02-06-00753 | EX.7 | A"-ground | axial wall mounted | 2400 | 10 | 5 | 0.6 |  | 1/220/50
02-06-00754 | EX.8 | A"-ground | axial wall mounted | 450 | 10 | 3.5 | 0.2 |  | 1/220/50
02-06-00755 | EX.9 | A"-ground | axial wall mounted | 700 | 10 | 3 | 0.2 |  | 1/220/50
02-06-00756 | EX.10 | A"-ground | axial wall mounted | 3400 | 10 | 6 | 0.6 |  | 1/220/50
02-06-00757 | EX.11 | A"-ground | axial wall mounted | 1900 | 10 | 4 | 0.4 |  | 1/220/50
02-06-00758 | EX.1 | C1 | propellen | 2550 | 10 | 4 | 0.2 |  | 1/220/50
02-06-00759 | EX.2 | C2 | propellen | 1100 | 10 | 0 | 0.1 |  | 1/220/50
02-06-00760 | EX.3 | A" | propellen | 850 | 10 | 3 | 0.1 |  | 1/220/50
02-06-00761 | EX.5 | doct | propellen | 1000 | 10 | 0 | 0.08 |  | 1/220/50
02-06-00762 | EX.4 | general | propellen | 500 | 80 | 0 | 0.07 |  | 1/220/50
ROOF EXTRACTOR SCHEDULE
02-06-00763 | RE-5 | A"-first | roof extrachter | 1600 | 200 | 8 | 0.5 |  | 220/1/50
02-06-00764 | RE-6 | A"-first | roof extrachter | 500 | 200 | 5 | 0.2 |  | 220/1/50
02-06-00765 | RE-25 | A"-ground | roof extrachter | 1800 | 200 | 8 | 0.5 |  | 220/1/50
02-06-00766 | RE-26 | A"-ground | roof extrachter | 700 | 200 | 5 | 0.4 |  | 220/1/50
02-06-00767 | RE-27 | A"-first | roof extrachter | 1300 | 200 | 5 | 0.4 |  | 220/1/50
02-06-00768 | RE-36 | A"-first | roof extrachter | 500 | 200 | 3 | 0.1 |  | 220/1/50
02-06-00769 | RE-17 | B-ground | roof extrachter | 300 | 200 | 5 | 0.2 |  | 220/1/50
02-06-00770 | RE-18 | B-ground | roof extrachter | 1200 | 200 | 15 | 2 |  | 3/380/50
02-06-00771 | RE-19 | B-ground | roof extrachter | 3400 | 200 | 12 | 2 |  | 3/380/50
02-06-00772 | RE-20 | B-ground | roof extrachter | 2210 | 200 | 12 | 2 |  | 3/380/50
02-06-00773 | RE-21 | B-ground | roof extrachter | 1530 | 200 | 10 | 2 |  | 1/220/50
02-06-00774 | RE-22 | B-ground | roof extrachter | 1020 | 200 | 8 | 0.7 |  | 1/220/50
02-06-00775 | RE-23 | A"-ground | roof extrachter | 2430 | 200 | 7 | 0.7 |  | 1/220/50
02-06-00776 | RE-35 | A"-ground | roof extrachter | 1000 | 200 | 6 | 0.7 |  | 1/220/50
02-06-00777 | RE-34 | A"-ground | roof extrachter | 500 | 200 | 5 | 0.5 |  | 1/220/50
02-06-00778 | battery charger
| 24 VDC/ UP TO 100 AMP | [8 empty] | 500
| 12 VDC/20 A | [8 empty] | 500
| 110 VDC/60A | [8 empty] | 500
| (12 - 96 ) VDC/10A | [8 empty] | 500
| variable (12-48)V / UP to 60 A | [8 empty] | 500
02-06-00779 | kerosene refrigertor 13ft | [8 empty] | 100
02-06-00780 | kerosene refrigertor 16ft | [8 empty] | 100
02-06-00781 | telephone exchange system | [8 empty] | 100
capasity :- 50 line
02-06-00782 | water treatment plans | [8 empty] | 100
first :plan componemts
| 1- primary water tank (1m^3) | [8 empty] | 100
| 2- duplex primary water pumps (6m^3/h,2.5bar | [8 empty] | 100
| 3-pirmary filters (25u) | [8 empty] | 100
| 4-duplex water softeners (cataionic,5m^3/h) | [8 empty] | 100
| 5-seconddry filters (5u) | [8 empty] | 100
| 6-duplex revers osmosis units (750L/hr) | [8 empty] | 100
| 7-stainless steel final tanks 1.5m^3 | [8 empty] | 100
| 8-duplex finaly water pumps (6m^3/h , 2.5 bar) | [8 empty] | 100
| 9-distillation water electrical system (750L/hr) | [8 empty] | 100
second:special conditions
1-seller should install , operate and check the plant
2-seller should supply 5 - years spare parts
3- seller should supply operation and maintenance catologes
4- seller should train the technical staff during installation and intiol start-up in site and factory
02-06-00783 | fire water pump
| typ | power | REV sec | suction MM | dishiarge MM |  | capacity L.S | head M
| horizontal | 3 | 1500 | 73.2 | 73.2 |  | 5 L.S | 15m |  | 100
02-06-00784 | water pump for tank
| typ | power | REV sec | suction MM | dishiarge MM |  | capacity L.S | head M
| horizontal | 0.75 | 1500 | 24.4 | 24.4 |  | 1.5 L.S | 15m |  | 100
electrical distribution
| item |  | no. of phases |  | no. of polese |  | voltage | amper
02-06-00785 | circuit breaker |  | 3 |  | 4 |  | 380V | 60A |  | 1000
02-06-00786 | contractor |  |  |  | 4 |  | 380v | 60A-40A |  | 1000
02-06-00787 | over load |  |  |  | 3 |  | 380v | 60A-40A |  | 1000
02-06-00788 | switch | [5 empty] | 380v |  |  | 1000
02-06-00789 | oxygen suplply station and equipment | [8 empty] | 100
02-06-00790 | flometer oxygen center : adapter | [8 empty] | 100
02-06-00791 | telephone instrument
| telephone instrument:- analogve type using both tone and pulse dialing ,suitable for electronic and cross bar exchanges | [8 empty] | 20000
fan coil unit
| No. of fan | No. of motor |  | type of fan coil unit |  | water temp. (in-out)c |  | capacity (ton) |  | Qty.
02-06-00792 | 2 | 1 |  | chiding horizontal |  | 90 |  | 20 |  | 500
02-06-00793 | 21 | 21 |  | chiding horizontal |  | (6 - 10) , (15 - 20) |  | (1/4) |  | 500
02-06-00794 | 2 | 1 |  | chiding horizontal |  | (8 - 12) |  | (2-3) |  | 500
02-06-00795 | 2 | 1 |  | chiding horizontal |  | _ |  | 1 |  | 500
02-06-00796 | motor control board
complete motor control board , 3ph , star - delta starting with all nessecery contacters and fuses and protection devises , the power of the motor as bellow
| 3.5KW | [8 empty] | 200
| 4.5KW | [8 empty] | 200
| 5.5KW | [8 empty] | 200
| 15KW | [8 empty] | 200
| 11.5KW | [8 empty] | 200
| 55KW | [8 empty] | 200
| 75KW | [8 empty] | 200
| 22KW | [8 empty] | 200
| 30KW | [8 empty] | 200
02-06-00797 | briller type writer | [8 empty] | 500
german type (portable)
02-06-00798 | record cassette japanese from (60) minate | [8 empty] | 2000
02-06-00799 | record cassette (with out radio) japanese origin or european origin | [8 empty] | 500
02-06-00800 | full set of kits for repairingmaintainins equpment (microelectronic equpment) hearing aids | [8 empty] | 100
02-06-00801 | computer screen for weak resion person (weak sighted ) | [8 empty] | 100
02-06-00802 | duplicator recorder cassette | [8 empty] | 100
02-06-00803 | electrical fitting
| required matrial |  |  | power |  | voltage |  | size |  | qty.
| fluoresent |  |  | 35W |  | 220V |  | TLD 4x35 |  | 2000
02-06-00804 | chilled water pump
| kw | r.p.m | Q L/S | Hm | QTY
| 4 | 1500 | 41 | 7.5 | 500
| 5.5 | 1500 | 20 | 20 | 500
| 11 | 1500 | 27 | 35 | 500
| 15 | 1500 | 30 | 30 | 500
| 22 | 1500 | 65 | 24 | 500
| 30 | 1500 | 42 | 42 | 500
| 20 | 3000 | 45 | 24 | 500
02-06-00805 | water pump forsenitary (hot water)
| kw | r.p.m | Q L/S | Hm | QTY
| 3 | 3000 | 8.3 | 32 | 500
| 5.5 | 1500 | 7 | 35 | 500
| 11 | 3000 | 5.5 | 50 | 500
02-06-00806 | water pump for tank
| kw | r.p.m | Q L/S | Hm | QTY
| 0.75 | 3000 | 1.5 | 60 | 1000
| 3 | 1500 | 5 | 30 | 1000
| 5.5 | 1500 | 10 | 30 | 1000
| 7.5 | 1500 | 40 | 20 | 1000
| 15 | 1500 | 16.6 | 44 | 1000
| 22 | 1450 | 28 | 40 | 1000
| 7.5 | 3000 | 1.25 | 85 | 1000
02-06-00807 | 1) Galvanized Steel Pipes And Fittings
Galvanized steel pipes and fitting conforming to BS 1387 or equivalent with 10 bar working pressure, all joints shall be screwed to B.S. 21 up to 50mm diameters, on large diameters (65mm and over) flanged joints shall be used.
Flange shall be conforming to B.S 4504 part 1.
| 1-1) Piping:- O 15 mm (6m length /piece) | [8 empty] | Pieces | 2500
| O 20 mm | [8 empty] | = | 2000
| O 25 mm | [8 empty] | = | 1500
| O 32 mm | [8 empty] | = | 1000
| O 40 mm | [8 empty] | = | 1000
| O 50 mm | [8 empty] | = | 1500
| O 65 mm | [8 empty] | = | 1000
| O 75 mm | [8 empty] | = | 1000
| O 100 mm | [8 empty] | = | 500
1-2) Ditto:- but with 15 bar working pressure
| O 100 mm (6m length / piece) | [8 empty] | Pieces | 500
| O 150 mm | [8 empty] | = | 300
02-06-00808 | 2) Copper Pipes And Fittings
2-1) Copper tubes and compression or capillary fittings to BS 2871 part 1 table x
| O 10 mm | [8 empty] | M.L | 5000
| O 15 mm | [8 empty] | = | 7500
| O 22 mm | [8 empty] | = | 7500
| O 28 mm | [8 empty] | = | 7500
| O 35 mm | [8 empty] | = | 5000
| O 42 mm | [8 empty] | = | 5000
| O 54 mm | [8 empty] | = | 5000
| O 67 mm | [8 empty] | = | 5000
| O 76.1 mm | [8 empty] | = | 6000
| O 108 mm | [8 empty] | = | 4000
| O 159 mm | [8 empty] | = | 3500
2-2) Ditto:- but to BS 2871 part 1 table T with fittings
| O 35 mm | [8 empty] | M.L | 3000
| O 42 mm | [8 empty] | = | 3000
| O 54 mm | [8 empty] | = | 5000
| O 67 mm | [8 empty] | = | 4000
| O 76.1 mm | [8 empty] | = | 4000
| O 108 mm | [8 empty] | = | 3500
02-06-00809 | 3) Ductile Iron Pipe And Fittings
Ductile iron pipes and fittings according to BS 4772 jointing should be flanged type with rubber gasket with 15 bar working pressure.
| O 75 mm (6 m length / piece) | [8 empty] | Pieces | 500
| O 100 mm | [8 empty] | = | 750
| O 125 mm | [8 empty] | = | 750
| O 150 mm | [8 empty] | = | 1000
| O 200 mm | [8 empty] | = | 2000
| O 250 mm | [8 empty] | = | 1500
| O 300 mm | [8 empty] | = | 1500
| O 350 mm | [8 empty] | = | 1500
| O 400 mm | [8 empty] | = | 1000
02-06-00810 | 4) Cast Iron Pipes And Fittings
4-1) Socketless cast iron pipes and fittings in
accordance with BS 437 or equivalent for drain pipes and fittings complete with coupling and rubber gasket
| O 50 mm (3m length / piece) | [8 empty] | Pieces | 1000
| O 75 mm | [8 empty] | = | 500
| O 100 mm | [8 empty] | = | 1250
| O 150 mm | [8 empty] | = | 1000
| O 200 mm | [8 empty] | = | 1000
| O 250 mm | [8 empty] | = | 1200
| O 300 mm | [8 empty] | = | 750
4-2) Ditto, but conform to BS 416 for soil, waste and ventilation
| O 50 mm (3m length / piece) | [8 empty] | Pieces | 750
| O 75 mm | [8 empty] | = | 500
| O 100 mm | [8 empty] | = | 1000
| O 150 mm | [8 empty] | = | 500
| O 200 mm | [8 empty] | = | 350
4-3) Ditto, but conform to BS 460 for roof drainage
| O 75 mm (3m length / piece) | [8 empty] | Pieces | 250
| O 100 mm | [8 empty] | = | 750
| O 150 mm | [8 empty] | = | 300
4-4) Ditto, but for roof outlets
- vertical type
| O 75 mm | [8 empty] | NOS | 50
| O 100 mm | [8 empty] | = | 100
| O 150 mm | [8 empty] | = | 70
- horizontal type
| O 75 mm | [8 empty] | NOS | 50
| O 100 mm | [8 empty] | = | 100
| O 150 mm | [8 empty] | = | 60
02-06-00811 | 5) Sectional Pressed Steel Tanks
Sectional pressed steel tanks shall be consists of (1x1)m dimensions galvanized plates modular or (1.22 x 1.22) m to BS 1564. All plates shall be of 6 mm thickness, the cover shall be of 3 mm thickness. The tanks have compartments. The tank plate shall be of external flange construction and bolting with suitable gasket materials. All piping connections shall be flanged type.
The tank should be provided with all necessary accessories such as floats ventilators, manhole opening, inside and outside ladder, over flow and drain pipes with level indicator …. Etc.
Strip jointing must be provided for all joints.
| 5-1) Pressed steel tank of 100 m³ | [8 empty] | No. | 1
| 5-2) Pressed steel tank of 280 m³ | [8 empty] | No. | 1
02-06-00812 | 6) Water Service Booster Pump Set
6-1) Three centrifugal pumps, direct coupled,
end suction type arranged to run as two duty/one
standby. The pumps have the following
specifications:
Q= 15m³/hr - H= 65m
Casing:- cast iron
Impeller:- bronze
shaft:- stainless steel
Seal:- mechanical
Insulation:- class F
IP:- 54 suitable for 380V/ 3pH/ 50Hz
6-2) Two pneumatic pressure vessel of 2m³ capacity and 10 bar working pressure.
complete with oil free compressor
6-3) All necessary accessories such as isolating
valves on suction and discharge, non return valves, pressure and flow gauges, pressure swtiches….etc.
6-4) Control panel
| The whole assembly shall be mounted on a purpose mode base from complete with steel pipe work, pipe supports and lifting lugs. | [8 empty] | unit | 1
02-06-00813 | 7) Fire Fighting Pumps Set (Wetriser)
7-1) Ditto, as item 6-1, but two multistage pumps (horizontal type, one duty / one stand by)
Q= 90 m³/hr
H= 90M
7-2) Ditto, as item 6-1, but one pump multistage vertical type with Q= 10m³/hr
H= 90M (as Jocky pump)
7-3) Ditto, as item 6-3
| 7-4) Ditto as item 6-4 | [8 empty] | unit | 1
02-06-00814 | 8) Fire Fighting Pumps Set (Hose Reel)
| Ditto, as item (7), but without providing Jocky pump. Q= 8m³/hr - H=75m | [8 empty] | unit | 1
02-06-00815 | 9) Drainage Submersible Pumps Set
Fully automatic drainage pump set, comprises of two pumps, non clogging type, motor squirrelcage, 3pH with class F insulation, complete with guide rails for retaining pump position, and chain shall be attached to the pump. The set shall be complete with isolating valves, non return valves, pressure swtiches...etc. Electrical floats shall be provided to control water level.
Casing:- cast iron
Impeller:- cast iron
shaft:- stainless steel
Seal:- mechanical
| 9-1) Q= 25m³/hr - H=10M | [8 empty] | unit | 10
| 9-2) Q= 20m³/hr - H=12M | [8 empty] | unit | 10
| 9-3) Q= 15m³/hr - H=12M | [8 empty] | unit | 10
| 9-4) Q= 10m³/hr - H= 10M | [8 empty] | unit | 10
| 9-5) Q= 5m³/hr - H=12M | [8 empty] | unit | 10
02-06-00816 | 10) Sewage Submersible Pumps
Ditto for sewage submersible pumps:
| 10-1) 20m³/hr - H=10M | [8 empty] | unit | 10
| 10-2) 10m³/hr - H=10M | [8 empty] | unit | 10
| 10-3) 5m³/hr - H=12M | [8 empty] | unit | 10
| 10-4) 3m³/hr - H=12M | [8 empty] | unit | 10
02-06-00817 | 11) Circulating Pumps Units
Electrical inline circulator pumps with vairable velocities. Motor of non-over loading characteristics with by passarrangement, valves, timer… etc. The unit shall be complete with control panel.
| Q= 5m³/hr - H=12 | [8 empty] | unit | 8
02-06-00818 | 12) Make-up Boosting Pumps Set (Cooling Tower)
Ditto as item 6 but with the following specification:-
Q= 20m³/hr
H= 35M
| Complete with two diaphram pressure vessel of capacity 500 liter per each. | [8 empty] | unit | 1
02-06-00819 | 13) Water Softener
Fully automatic douplex softener complete with necessary accessories such as piping, valves, flow meters, pressure gauges complete with control panel … etc.
Flow rate= 20m³/hr
Inlet pressure= 1.5bar
| working pressure= 10bar | [8 empty] | unit | 1
02-06-00820 | 14) Heavy Duty Filters
Fully automatic packaged unit high rate muliti-layered sand filters complete with main operating valves , pipes and fitting ,flow control , controls, filter media and accessories such as pressure gauges ,cocks for inlet and outlet with 10 bar working pressure.
| 14-1) Flow rate 30 m3/hr | [8 empty] | No. | 1
| 14-2) Flow rate 60 m3/hr | [8 empty] | No. | 1
02-06-00821 | 15) Actived carbon Filters
Ditto , but with activated carbon beds with 10 bar working pressure
| 15-1) Flow rate 25 m3/hr | [8 empty] | No. | 1
| 15-2) Flow rate 50 m3/hr | [8 empty] | No. | 1
02-06-00822 | 16) Cast iron adaptor
16-1) Cast iron ( mentioned in item 4 ) adaptor to be connected with upvc pipes conform to BS 4514 . For soil and ventilating pipe :
| 50 mm | [8 empty] | Nos | 100
| 75 mm | [8 empty] | Nos | 80
| 100 mm | [8 empty] | Nos | 100
| 150 mm | [8 empty] | Nos | 60
| 200 mm | [8 empty] | Nos | 45
16-2) Ditto but be connected with pvc pipes
| 50 mm | [8 empty] | Nos | 150
| 75 mm | [8 empty] | Nos | 75
| 100 mm | [8 empty] | Nos | 90
| 150 mm | [8 empty] | Nos | 50
02-06-00823 | 17) Flexible Hose
17-1) Rubber flexible hose used for connection between sanitary fixture and feeding water pipes :-
| working pressure 3.5 bar diam 15 mm | [8 empty] | Nos. | 300
| 17-2) Ditto, but copper hose working pressure 7 bar diam 15 mm | [8 empty] | Nos. | 500
02-06-00824 | 18) Sanitary Fixtures
Vitrus china (or equivelant) sanitary fixtures of white colour .All fixtures shall be of the best quality .
| 18-1) Eastern style we ( 100 mm s trap) supplied with vitrus china cistern of 14 lit capacity complete with ball valve and float .All wcs shall be provided with accessories. | [8 empty] | Nos | 80
| 18-2) Ditto , but "P" trap | [8 empty] | Nos | 75
| 18-3) Ditto , but westeren style wc supplied with cast iron cistern of 14 lit-capacity complete with ball valve and flood, chain.All wc's shall be provided with 32 mm flush pipe and 15 mm chromium flexible hose of 0.75m length and 3.5 bar resisting pressure.The hose completed with 10 mm chromium nozzle. | [8 empty] | Nos | 70
18-4) Ditto ,but wash basin complete with vitrus china stands, shelfs and soap trys.All the wash basins shall be provided with:-
25mm chromium bottle (or"p") trap
| 15mm chromium plated mixer and 3.5 bar resisting pressure | [8 empty] | Nos. | 300
18-5) Ditto ,but bedit complete with:-
- 40 mm chromium plated bottle trap ( or ‘P’)
| -15 mm chromium mixer and 3.5 bar resisting pressure. | [8 empty] | Nos. | 100
18-6) Cast iron shower tray , complete with 15 mm chromium plated mixer with 15 mm flexible chrom. Hose ended with chrom. head shower ( resisting pressure 3.5 bar ) .The flexible hose has the alternative of being fixed on wall.Complete with all accessories such as soap tray …etc
| - Tray size 800x800 | [8 empty] | Nos | 100
18-7) Ditto, but bath tub , complete with
| 15 mm chromium mixer with 15 chromium tube with head shower .The bath shall be provided with MM 15 chromium flexible hose ended with shower . All the bath tubs shall be provided with accessories such as soap tray , chromium handle , 40 mm chromium bottle ‘p’ trap | [8 empty] | Nos | 50
18-8) Ditto as 18-5, but for urinal complete with
- 9 lit vitrus china automatic cisteren complete with flushing pipe
- 32 mm chromium plated bottle trap (‘p’ trap )
| - partitions | [8 empty] | Nos | 60
02-06-00825 | 19) Grease+B778+B753 Trap+B742+B726
| Cast iron grease trap with 100 MM mm outlet with access at ground level, supplied with single seal cover and frame and screwed flange for 50 mm vent , supplied with galvanized sediment pans . | [8 empty] | Nos | 30
02-06-00826 | 20) Covers and Frames
20-1) Medium duty double sealed cast iron cover and frames with the following size :
| REF! C25525 mm | [8 empty] | Nos. | 120
| - 600 x 450 mm | [8 empty] | Nos. | 50
| - 900 x 600 mm | [8 empty] | Nos. | 70
20-2) Ditto, but heavy duty
| - Diam 550 mm | [8 empty] | Nos. | 200
20-3) Ditto, but heavy medium grating and frames
| 600 x 450 | [8 empty] | Nos. | 100
20-4) Ditto, but for Hydrant cover and frame
| 500 x 350 | [8 empty] | Nos. | 100
20-5) Ditto, but special purpose covers and frames have a single seal and supplied with 4 brass screws.
| The top is recessed for filling to material match the surrounding surfaces. | [8 empty] | Nos. | 75
20-6) Ditto, but roadway gratings and frames
| 500 x 350 | [8 empty] | Nos. | 500
20-7) Ditto, but heavy duty cast iron channel grating , supplied with lugs cast at 30 cm centers.
| Size 100 x 30 cm | [8 empty] | Nos. | 500
02-06-00827 | 21) Pillar Fire Hydrant
| 21-1) A piller fire hydrant consists of a body equipped with "3" nozzles , one forward 100 mm and two side ways 65 mm . The body projects a bove ground level .The valve box containing the closure device below ground between these two main 100 mm diam. stand pipe , the hydrant shall be completed with a screw - down system for opening and closing , automatic drainage device and on air inlet device . All the iron fire hydrant are coated with red polyurethane paint , the threading shall be to BS 750 | [8 empty] | Nos. | 50
| 21-2) Ditto,but consists of 2 nozzels 80 mm forward nozzel and 65 mm side way nozzel | [8 empty] | Nos. | 50
21-3) Ditto , but fire and washing hydrant consists of iron body . The box enclosing on outlet nozzel . It has a detachable ductile iron lid.
| 80 mm hydrant | [8 empty] | Nos | 50
65mm nozzel
02-06-00828 | 22) Hose Real & Wet Riser / Cabinet
22-1) Hose real cabinet accomodates a manually or automatically operated swinging hose reel which can be combined with a matching wer riser or extinguisher cabinet .
Door have right opening and swing through a full 180 :
Size :- 1350 x 810 x 355 mm
Construction :- steel . Door panel shall be provided with stainless steel finger panel
Capacity :- 30 x 19 mm dia
Nozzle :- jet ( hose reel )
| Pressure:- max. operation pressure 10 bar | [8 empty] | Nos. | 25
22-2) Ditto, swinging open wall hose reel
Diam:- 560 mm
Overall height:- 610 mm
| Width:- 250 mm | [8 empty] | Nos. | 10
02-06-00829 | 23) Dimener lized water
Full automatic , Duplex Dimenerlizer complete
with necessary accessories such as piping ,
regulating valves ,valves , flow meters , pressure
gauges complete with control panel ….etc.
- flow meter 25 m3/hr
- inlet pressure 1.5 bar
| - working presure 10 bar | [8 empty] | set | 1
02-06-00830 | 24) Distilled Water
Ditto , but Duplex Distiller , but of flow rate
| 20 m3/hr | [8 empty] | set | 1
02-06-00831 | Centrifugal Water Chiller
Type - Centrifugal , water cooled
Compressor and motor
The compressor - motor combination shall be Hermatic
construction complete with starter and capacitor for
power factor correction .The motor power is 3-phase
380 volt, 50 HZ with main power factor of o.91 at full
load
Cooler and Condenser
Cooler and condenser shall be shell and tube designed for
( 10 ) atm water side working pressure
Control Panel
Automatic control panel shall be electronic type including
all safety devices.
Evaporator Data
Fouling factor =0.0002
m2.hr.Cْ/Kcal
Ent. Water temp .=11.6Cْ
Leav. Water temp .=6 Cْ
Max. water pressure drop =6 M.water Gauge
Condenser Data
Fouling factor= 0.0004
m3.hr.Cْ/kcal
Ent. Water Temp = 29.4 Cْ
Leav. Water Temp =35 Cْ
Max. water pressure drop =7 M.water Gauge
Capacity
| 1200 000 kcal/hr | [8 empty] | 4 | Nos.
( 400 ton )
02-06-00832 | Hot Water Boiler
Type IN _ LINE
Electric
Tank
shall be constructed from low carbon steel - working
pressure 7.5 bar
Heating
Elements shall be of immersion type copper sheath of
11.6 watt/cm2 max.density
Control
proportional temperature control with multi - step control
complete with control board and all safety devices
| capacity 650 kw | [8 empty] | Nos | 4
02-06-00833 | Pumps
Type
End - section centrifugal oase mounted , direct coupled
Impeller Material
Bronze
Shaft material
stainless steel
seal -Mechanical
Motor
squirrel cage, drip proof type 1450 R.P.M
Base Material
cast iron or welded steel
chiled water pump capacity 61 L/S
| Head 45 m | [8 empty] | Nos. | 4
Hot water pump capacity 14 L/S
| Head 42 m | [8 empty] | Nos. | 4
Condenser water pump
capacity 76 - L/S
| Head 18 m | [8 empty] | Nos. | 4
02-06-00834 | Cooling Tower
Type- outdoor
forced draft
casino - hot dip
galvanized steel of min thickness 1.6 mm
Lowers , eliminators
and air inlet screen are hot dip galvanized steel
Full: shall be polyvinal
Basin-
shall be hot dip galvanized steel of min - thickness 3.5 mm
Water distribution
shall be galvanized steel pipes with bronze non - clog
spray nozzles
Motors
Outdoor use with class " F" insulation
Electric power
3 phase / 380v/50HZ
Water Temp
IN- 35 Cْ
out 29.4 Cْ
Out door wet bulb
temp- 27 Cْ
Heat Rejection Capacity
| 1500 000 K cal/ HR | [8 empty] | Nos | 4
02-06-00835 | Roof Top Packaged
A/C unit - Air Cooled
Max ambient outdoor working temp -52Cْ
Entering Air temp to condenser -46Cْ
Unit shall be complete with filter thermostat
| Capacity 69000 kcal/hr | [8 empty] | Nos. | 10
| Capacity 56000 kcal/hr | [8 empty] | Nos. | 8
| Capacity 45000 kcal / hr | [8 empty] | Nos. | 8
| Capacity 33000Kcal / hr | [8 empty] | Nos. | 6
02-06-00836 | Roof Ventilator
Horizantal dischange
Power 400v/3ph/50 hz
Unit shall be complete with back draught
shutter, bird guard
local isolating switch
and speed control
External static
pressure 6mm .W.G
| Capacity 1200 m3/hr | [8 empty] | Nos. | 10
| Capacity 2000 m3/hr | [8 empty] | Nos. | 10
| Capacity 3000 m3 /hr | [8 empty] | Nos. | 10
| Capacity 4000 m3/hr | [8 empty] | Nos. | 10
02-06-00837 | Supply Air Linear slot diffuser
Diffuser shall be constructed from Aluminum natural colour
solt width 19mm
integral volume control damper,fully adjustable from the face of the diffuser
complete with air deflection blode+B400s,mounting bracket.
| A) 3 SLOT | [8 empty] | M.L | 1000
| B) 4 SLOT | [8 empty] | M.L | 1000
| C) 5 SLOT | [8 empty] | M.L | 600
02-06-00838 | Supply Air square diffuser
alumin. construction
complete with volume control damper of opposed blade type
| A) size (neck)mm 225x225 | [8 empty] | Nos. | 200
| B) 300x 300 | [8 empty] | Nos. | 300
| C)375 x 375 | [8 empty] | Nos. | 300
02-06-00839 | Supply Air Re+B224gister
aluminum construction with volume control damper.
adjustable front horizantal bars and rear vertical adjus. bars
neck size ( B x H) mm
| 400 x 150 | [8 empty] | Nos. | 100
| 500 x 150 | [8 empty] | Nos. | 100
| 600 x 150 | [8 empty] | Nos. | 100
| 700 x 150 | [8 empty] | Nos. | 100
| 800 x 200 | [8 empty] | Nos. | 100
| 900 x 200 | [8 empty] | Nos. | 100
02-06-00840 | Exhaust Air Valve
shall be aluminum white colour
complete with counter frame nominal diameter mm
| Diam. 100 | [8 empty] | Nos. | 20
| Diam. 150 | [8 empty] | Nos. | 20
02-06-00841 | Piping
Black steel class B,schedule 40,with 10.5 Kg/cm2, seamless with fittings.B432
pipe size(mm diam.)
| 300 | [8 empty] | M.L | 500
| 250 | [8 empty] | M.L | 1000
| 200 | [8 empty] | M.L | 1000
| 150 | [8 empty] | M.L | 2000
| 125 | [8 empty] | M.L | 2000
| 100 | [8 empty] | M.L | 3000
| 80 | [8 empty] | M.L | 3000
| 65 | [8 empty] | M.L | 3000
| 50 | [8 empty] | M.L | 5000
| 40 | [8 empty] | M.L | 5000
| 32 | [8 empty] | M.L | 5000
| 25 | [8 empty] | M.L | 5000
| 20 | [8 empty] | M.L | 5000
| 15 | [8 empty] | M.L | 5000
02-06-00842 | VALES
cast iron gate valve with flanges 10.5 kg/cm2
| 250 mm | [8 empty] | Nos. | 50
| 200 mm | [8 empty] | Nos. | 60
| 150 mm | [8 empty] | Nos | 60
| 125 mm | [8 empty] | Nos | 60
| 100 mm | [8 empty] | Nos | 60
| 80 mm | [8 empty] | Nos | 40
| 65mm | [8 empty] | Nos | 40
Bronze gate valve serewed end- non-rising stem
| 50 mm | [8 empty] | Nos | 100
| 40mm | [8 empty] | Nos | 100
| 32 mm | [8 empty] | Nos | 100
| 25mm | [8 empty] | Nos. | 100
| 20 mm | [8 empty] | Nos. | 100
| 15 mm | [8 empty] | Nos. | 200
02-06-00843 | Galvanized sheet steel
Galvanized sheet steel (duct moterial)
U.S steel gouge
| 18 | [8 empty] | TON | 25
| 20 | [8 empty] | TON | 50
| 22 | [8 empty] | TON | 50
| 24 | [8 empty] | TON | 25
02-06-00844 | Duct thermal insulation
| fiber glass.flexible blanket type.25mm thick with vapour barrier consisting of 0.05mm aluminium : foil reinforced with kraft paper and glass fibre .Density of 24 kg per cubic meter | [8 empty] | M² | 100 000
02-06-00845 | Pipe insulation
sectional fibre glass with aluminum density of 48 kg/m3, factor applied vapour barrier jacket of minimum 0.05 aluminium foil laminated to kraft paper reinforced with glass fibers.
insulation nominal thickness
Bore(mm) mm
up to 65 25
80-150 40
200 and larger 50
size (mm diam.)
| 300 | [8 empty] | M.L | 500
| 250 | [8 empty] | M.L | 1000
| 200 | [8 empty] | M.L | 2000
| 150 | [8 empty] | M.L | 2000
| 125 | [8 empty] | M.L | 3000
| 100 | [8 empty] | M.L | 3000
| 80 | [8 empty] | M.L | 3000
| 65 | [8 empty] | M.L | 5000
| 50 | [8 empty] | M.L | 5000
| 40 | [8 empty] | M.L | 5000
| 32 | [8 empty] | M.L | 5000
| 25 | [8 empty] | M.L | 5000
| 20 | [8 empty] | M.L | 5000
| 15 | [8 empty] | M.L | 5000
CABLES & WIRES
02-06-00846 | A) Power cables: -
Low tension cables stranded copper
conductors, PVC insulated, all cores color
colour coded PVC inner sheath, high 600/1000 V
impactPVC outer sheath black, rated voltage
voltage 600/1000vgenerally to BS 6346
or to VDE 0271 NYY-J 0.9.86.
| A-1) 4 x 2.5 mm² NYY-J | [8 empty] | M.L | 5000
| A-2) 4 x 4 mm² NYY-J | [8 empty] | M.L | 5000
| A-3) 4 x 6 mm² NYY-J | [8 empty] | M.L | 5000
| A-4) 4 x 10 mm² NYY-J | [8 empty] | M.L | 5000
| A-5) 4 x 16 mm² NYY-J | [8 empty] | M.L | 5000
| A-6) 3 x 25 + 16 mm² NYY-J | [8 empty] | M.L | 5000
| A-7) 3 x 35 + 16 mm² NYY-J | [8 empty] | M.L | 6000
| A-8) 3 x 50 + 25 mm² NYY-J | [8 empty] | M.L | 5000
| A-9 3 x 95 + 50 mm² NYY-J | [8 empty] | M.L | 5000
| A-10) 3 x 120 + 70 mm² NYY-J | [8 empty] | M.L | 5000
| A-11 3 x 150 + 70 mm² NYY-J | [8 empty] | M.L | 5000
| A-12) 3 x 240 + 120 mm² NYY-J | [8 empty] | M.L | 3000
| A-13 3 x 300 + 150 mm² NYY-J | [8 empty] | M.L | 3000
| A-14) 4 x 6 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-15 4 x 10 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-16) 4 x 16 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-17) 3 x 25 + 16 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-18) 3 x 35 +16 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-19) 3 x 50 + 25 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-20 3 x 70 + 35 mm² PVC/SWA/PVC | [8 empty] | M.L | 5000
| A-21) 3 x 70 + 35 mm² NYY-J | [8 empty] | M.L | 5000
02-06-00847 | B) Wires:
Single wires, copper stranded core PVC
insulated, rated 70 permanent and160c
short circuit,rated voltage 450/750v
generlally to BS 6004 or to vde 0250
type nya
Packing: 100 yds each coil in specified.
colours
B-1 2.5 mm²
| Red | [8 empty] | Coils | 1500
| Black | [8 empty] | Coils | 1500
| Blue | [8 empty] | Coils | 1500
| Yellow | [8 empty] | Coils | 1500
| Grn/Ylw | [8 empty] | Coils | 1500
B-2 1.5 mm²
| Red | [8 empty] | Coils | 1000
| Black | [8 empty] | Coils | 1000
| Blue | [8 empty] | Coils | 1000
| Yellow | [8 empty] | Coils | 1000
| Grn/Ylw | [8 empty] | Coils | 1000
B-3 4mm²
| Red | [8 empty] | Coils | 500
| Black | [8 empty] | Coils | 500
| Blue | [8 empty] | Coils | 500
| Yellow | [8 empty] | Coils | 500
| Grn/Ylw | [8 empty] | Coils | 500
B-4 6mm²
| Red | [8 empty] | Coils | 500
| Black | [8 empty] | Coils | 500
| Blue | [8 empty] | Coils | 500
| Yellow | [8 empty] | Coils | 500
| Grn/Ylw | [8 empty] | Coils | 500
02-06-00848 | Telephone Cables & Accessories
A) Telephone cables: -
PVC/Bare copper conductor 0.6mm/tinned /PVC
| A-1) 10 pair. | [8 empty] | M.L | 5000
| A-2) 20 pair. | [8 empty] | M.L | 5000
| A-3) 30 pair. | [8 empty] | M.L | 5000
Packing: on wooden drums.
B) Accessories: -
Terminal Box-Flush Mounted
Steel Grey / rust proof + Terminal block.
| B-1) 10 pair. | [8 empty] | No. | 50
| B-2) 20 pair. | [8 empty] | No. | 50
| B-3) 30 pair. | [8 empty] | No. | 50
| B-4) 100 pair. | [8 empty] | No. | 20
02-06-00849 | Conduit & Accessories
A) Size 20mm: -
A-1 Hot dip galvanized heavy gauge steel conduit, screwed both ends, one coupler, 3.75m long to BS 4568.
| coupler, 3.75m long to BS 4568. | [8 empty] | Cond | 10000
A-2 Galvanized circular malleable iron
junction boxes.
| Terminal | [8 empty] | No. | 2000
| Through | [8 empty] | No. | 5000
| Angle | [8 empty] | No. | 2000
| Tee | [8 empty] | No. | 2000
| Intersection | [8 empty] | No. | 3000
B) Size 25mm: -
| B-1 Hot dip galvanized heavy gauge steel | [8 empty] | Cond | 5000
conduit, screwed both ends, one coupler,
3.75m long to BS 4568.
B-2 Galvanized circular malleable iron
junction boxes.
| Terminal | [8 empty] | No. | 1000
| Through | [8 empty] | No. | 1000
| Angle | [8 empty] | No. | 1000
| Tee | [8 empty] | No. | 1000
| Intersection | [8 empty] | No. | 1000
C) Draw in steel tape: -
| C-1 20m length | [8 empty] | No. | 50
| C-2 30m length | [8 empty] | No. | 50
D) Complete set comprising stock
dies & guides: -
| D-1 20+25 mm | [8 empty] | set | 20
02-06-00850 | A -Panel distribution boards:
Three-phase and neutral distribution
borads voltage 415v AC 50 HZ BS 5486
IP230 with door and lock
to fixed in the wall (flush type) with
Earthling terminal bus bars and with
| A-1 Distribution board 6 triple pole MCB | [8 empty] | NOS. | 25
ways
Main in coming 100A MCB three phase
Single poles MCB 15A.10 .NOS
Single poles MCB 30A 8Nos.
| A-2 Distribution board 8 triple pole MCB | [8 empty] | NOS. | 25
ways-
Main in coming 100A MCB three phase
Single poles MCB 15A 15 NOS.
Single poles MCB 30A 9NOS.
| A-3 distribution bord 12 triple pole mcb | [8 empty] | NOS | 25
warpmain Incoming 160 mcb three phase
single pole mcb 15 A 20 Nos
single pole mcb 30 A 16 Nos
A-4 SPARES
| single pole mcb 15 A | [8 empty] | NOS | 100
| single pole mcb 30 A | [8 empty] | NOS | 100
02-06-00851 | Switches and Sockets
A- SWITCHES
Switches 250v 15 or 20 amp
fluch mounting-white cover
| A-1 one way 1 gang | [8 empty] | NOS | 500
| A-2 two way 1 gang | [8 empty] | NOS | 500
| A-3 one way 2 gang | [8 empty] | NOS | 500
| A-4 one way 2 gang | [8 empty] | NOS | 500
| A-5 one way 3 gang | [8 empty] | NOS | 500
| A-6 one way 4 gang | [8 empty] | NOS | 500
B-SWITCHES SOCKETS
3 pin Rectangular bs 2814- 13 or 15 Amp
Fluch mounting-white cover Bs 1863
| B-1 3pin rectangulaectan-13 Amp | [8 empty] | NOS | 5000
| B-2 3pin rectangulaectan-Duplex13 Amp | [8 empty] | NOS | 5000
| B-3 3pin rectangulaectan-15 Amp | [8 empty] | NOS | 5000
| B-4 2Amp Telephone socket | [8 empty] | NOS | 5000
| B-5 T.Vsocket single out let | [8 empty] | NOS | 1000
02-06-00852 | Fire Alarm System
A-1) central Indication and control panel
suitable for 6 fire zones with fire alarm
bell complete with all safety device and
outomatic charger including nickel
cadmium battery with connection to the
| central Indicationg and control board | [8 empty] | No.C741 | 1
A-2)Manual call station break glass units-
surface mounted- red coulour the glasses
| can be supplied in english language | [8 empty] | NOS | 15
A-3) complete with amounting base outomatic
smoke detector off white coulor withvisual
of an alarm is given by red light diode
clearlyn visble on the detector casing
| ambient temp range (0c- 50c) | [8 empty] | NOS | 70
A-4)complete with a amounting base amount-
ing heat detector with visual Indication
of an alarm is given by red- light diode,
clearly visble on detector with base off
| white colour ambient range (0c- 40c) | [8 empty] | NOS | 10
A-5) Indoor fire alarm bell 24v.Ds black poly-
carbonete base.6" hight reliability, long
running life and easy installation,nomain-
| tenace in normal use. | [8 empty] | NOS | 15
02-06-00853 | Light fittings: -
NOTE:
Below mentioned fluorescent fittings .
are security quick startPower factor not
lessthan 0.9 Lagging 240 volt-AC 50HZ.
A-1) 2 x 40w fluorescent fitting with Lamella
| louver -recessed mouting | [8 empty] | NOS | 400
A-2) 2 x 40w fluorescent fitting with Lamella .
| louvre-Surface mounting | [8 empty] | NOS | 250
A-3) 1 x 40w fluorescent fitting with Lamella
| lovre-Recessed mounting. | [8 empty] | NOS | 400
A-4) 1 x 40w fluorescent fitting with Opal
| Diffuser-Surface mounting. | [8 empty] | NOS | 250
A-5) 2 x 20w fluorescent light fitting with
| Opal Diffuser-Surface mounting. | [8 empty] | NOS | 500
A-6)4 x 20w fluorescent light fitting with
| Opal Diffuser-Surface mounting. | [8 empty] | NOS | 500
| A-7)60 X 60 cm Fluorescent light with lamela diffuser | [8 empty] | NOS | 400
02-06-00854 | Aluminum false ceiling closed type with all fixing accessories
| 30 x 60 cms | [8 empty] | M² | 4000
| 30 x120 cms | [8 empty] | M² | 4000
| 60 x 60 cms | [8 empty] | M² | 12000
| 10 x 360 cms | [8 empty] | M² | 5000
| suspension accessories and angle bead | [8 empty] | M² | 25000
02--06-00855 | Door closers Yale type or equivalent with all accessories | [8 empty] | No. | 100
02--06-00856 | Expansion joint beads made of stainless steel, 0.5mm thick | [8 empty] | M.L | 500
| Floor type | [8 empty] | M.L | 200
| Wall type | [8 empty] | M.L | 450
| Ceiling type | [8 empty] | M.L | 100
02-06-00857 | Special doors frames and door leaves different dimensions,with door handles (cylinder and bath). | [8 empty] | No. | 450
02-06-00858 | Anti static Vinyl tiles 120cm width, 3.5 mm thickness, with welding rods and fixing materials. | [8 empty] | M² | 500
02-06-00859 | Ceramic tiles 10 x 10 cm, 6mm thick, non-slip ceramic | [8 empty] | M² | 3500
02-06-00860 | Epoxy paints for walls | [8 empty] | Lit | 3000
02-06-00861 | Metal Lath 60 x 240 cm, weight 1.7 kg/m2 | [8 empty] | M² | 5000
02-06-00862 | diesel pump
| HP | r.p.m | Q m^3/hr | Hm
| 60-75 | 1450 | 200 | 60 | 100
02-06-00863 | electrical pump
| HP | r.p.m | Q m^3/hr | Hm
| 60-75 | 1450 | 200 | 60 | 100
02-06-00864 | NON-ION IC WATER SYSTEM | [9 empty] | 100
1-capasity:-3-4 m^3/hr
2-conductivity (mixing 0f + and - ) :- (0.1 - 0.5)MS
3-raw water input
main components
1-primary water tank (1m^3)
2-two duplex primary water pumps (6m^3/hr , 2.5bar)
3-three primary filters (25 micron)
4-four duplex water softener (cationic , 5m^3/hr)
5-secondary filters (5micron)
6-two duplex mixed bed deionizer (3-4m^3/hr
air handling unit (AHU)
| type of fulter | power (KW) | no of motor | type of air (AHU) |  | connecti size on (in-out) for each coil | air flow |  |  | water floow m^3/hr |  | water temp (in-temp)C |  | capacity | qty
|  |  |  | other type | in-line |  | for cooling | for heating |  | for cooling | for heating | for cooling | for heating
02-06-00865 | type | 15 | 1 | _ | in line | 62.5mm | 8 12 | 8 12 |  | 102 | 45.5 | 8 12 | 8 12 | 350 | 6
02-06-00866 | type | 17 5.5 10 | 1 14 | _ | in line | in50mm out 50mm | 29153 | 29153 |  | 3581 | 1750 | 7.2 5 | 82.2 30 - 50 | 5000 | 7
02-06-00867 | type | 4.1 11 | 1 | _ | in line | 62.5 | 5500/ 2200 | 5500/ 2200 |  | 13 | 13 | 9 12 | 9 12 | 50 | 2
02-06-00868 | type | 3.75 | 1 | _ | in line | in36mm out 36mm | 11864 | 11864 |  | 15.12 | 5.34 | 7.3 | 82.2 | 5000 | 1
02-06-00869 | type | 7.5 | 1 | _ | in line | in50mm out 50mm | 26271 | 26271 |  | 21.36 | 6 | 7.2 | 82.2 | 5000 | 1
02-06-00870 | type | 7.5 | 1 | _ | in line | in36mm out 36mm | 22881 | 22881 |  | 21.12 | 7.32 | 7.2 | 82.2 | 5000 | 1
02-06-00871 | type | 7.5 | 1 | _ | in line | in50mm out 50mm | 23220 | 23220 |  | 39.48 | 17.96 | 7.2 | 82.2 | 5000 | 1
02-06-00872 | type | 9.3 | 1 | _ | in line | in50mm out 50mm | 25424 | 25424 |  | 51.7 | 21 | 7.2 | 82.2 | 5000 | 1
02-06-00873 | type | 5.625 | 1 | _ | in line | in50mm out 50mm | 15424 | 15424 |  | 31.32 | 12.81 | 7.2 | 82.2 | 5000 | 1
02-06-00874 | type | 9.3 | 1 | _ | in line | in50mm out 50mm | 29153 | 29153 |  | 59.5 | 24.4 | 7.2 | 82.2 | 5000 | 1
02-06-00875 | type | 2.25 | 1 | _ | in line | in50mm out 50mm | 8485 | 8485 |  | 14.7 | 7.2 | 7.2 | 82.2 | 5000 | 1
02-06-00876 | MZ | 7.5 | 1 | _ | in-line |  | 30 | 30 |  | 40 | 40 | 6 _ 12 | 82 | 200 lit/mm | 16
02-06-00877 | normal | 10KW | 1 | _ | in-line | 2" inch | _ | _ |  | _ | _ | 6_12 | 75-50 | 40 ton | 5
02-06-00878 |  | 7.5 | 7 | X | _ | 3inch | X | X |  | X | X | _7_ | 80 | 9500m^3/hr | 7
02-06-00879 | _ | 4 | 1 | _ | in-line | _ | 30 | 30 |  | 40 | 40 | _6_ | 60 | 72.000BTU/hr | 8
air handling unit (AHU)
| type of fulter | power (KW) | no of motor | type of air (AHU) |  | connecti size on (in-out) for each coil | air flow |  |  | water floow m^3/hr |  | water temp (in-temp)C |  | capacity
|  |  |  | other type | in-line |  | for cooling | for heating |  | for cooling | for heating | for cooling | for heating | for cooling | for heating
02-06-00880 | No.of AHU 15 N.B.S 35% | 18.5 | 1 |  | in line |  | 32.700 M^3/H | 32.700 M63/H |  | 655 L/Min | 107 L/Min | 7C/12C | 83/71C | 189.55 KAL/H | 68.200 KAL/H
02-06-00881 | No.of AHU 19 N.B.S 80% |  | 55 | 1 | in line |  | 64.900 M^3/H | 64.900 M^3/H |  | 1202L/Min | 233 L/Min | 7C/12C | 83/71C | 150.200 KAL/H | 400.200 KAL/H
fan coil unit
| no.of fan | no.of motor | type of fan coil unit |  |  |  | water temp. (In-out) | capacity (ton) |  | qnt.
|  |  | ground complete vertical |  | chiding horizontal
02-06-00882 | 2 | 1 | ground |  | _ |  | 9 12 | 2 |  | 52
02-06-00883 | 1 | 1 | _ |  | chiding horizontal |  | 70-11c | 3ton |  | 350
02-06-00884 | 1 | 1 | ground |  | _ |  | 70-11c | 2ton |  | 30
02-06-00885 | 1 | 1 | ground |  | _ |  | 70-11c | 2ton |  | 30
02-06-00886 | 1 | 1 | ground |  | _ |  | 70-11c | 2ton |  | 25
02-06-00887 | 3 | 1 | 10 |  | 18 |  | 6_12 | 40ton |  | 28
02-06-00888 | 4 | 20 | 10 |  | 10 |  | 10_12 | 2ton |  | 20
02-06-00889 | 2 | 2 | ground |  | _ |  | (5_10)c | 2ton |  | 100
02-06-00890 | cold stor | [8 empty] | 100
1-inside temperature (4-16C)
2-volume 20M^3
3-the cold store must be supplied with shade to from raining
4-ambiebient temperature 55C
5-the walls will be s and outs panel, the out side walls made from aluminum sheets at thickness 0.6mm and the inside walls made from aluminum sheet 0.6 mm,the out sid and the insid walls injected by polyethem with density 40KG/M^3, with thickness (100-120)mm
6-the floor made of jacker plane from aluminum
7-the door is hinged type
8-two cooling unit one work and the other stand by each unit is sufficient to keep inside temperature (4-16C)
9-the compressor is semi hermetic type
10-the cold store supplied with all the complete control (oil pressure,high-low pressure,thermostat,seloid valve pressure,high-low pressure,thermostat,seloid valve
02-06-00891 | refregrater | [8 empty] | 100
valume for refregrater 35foot^3
220V , 50HZ , 1phase
ferion:- R134
internal temperature ranging from +2to +6C
inside and out side material stainless steel
aolitle/visua/ alarm with battery , low alarm 0C , high alarm +10C
autamatic defrosting
out side thermometer or the door
7 day recorder
double compressor units for additionel/safety
removabe shalves inside
spar parts for 5 years
02-06-00892 | water ion exchenger | [8 empty] | 100
capacity:-20lit/hr
02-06-00893 | machine for sealing bottles of plastic & aluminum caps | [8 empty] | 100
02-06-00894 | centeral oxygen system | [8 empty] | 100
capasity:- 20 cylinder
1-tow stages (pressure)
a-first stage 160 :- 10Kg/cm^2
b- second stage 10 :- 4Kg/cm^2
right 10 clinder
lift 10 :- 4Kg/cm^2
control system 24V
| 2-nitrous system 2 clinder | [8 empty] | 100
a-first stage 60 - 9Kg/cm^2
b- second stage 9 - 4Kg/cm^2
control system 24V
| 3-midical gas | [8 empty] | 100
normal & stand by
compress air oilless 2
5 start Kg/cm^2
7stop Kg/cm^2
reducing valv for pressure
filter system
pressure lin 4Kg/cm^2
bottle for air
| 4-centeral - vacum | [8 empty] | 100
valume line
1-bottle
2-check valve
working pressure
start pressure (vacum) 300 mmg
stop 500 mm /Kg
300 - 500 mm/Kg
02-06-00895 | softener | [8 empty] | 100
continuos softener supply as following
1-max.flow :- 1m^3/hr
2-resin - strong cationic resin sodium base
3-power supply 220V or 380V 50HZ
02-06-00896 | high tension switch gear | [8 empty] | 100
vaccum type 11KV input - 420V out put -3ph -800A with complete protection devise
02-06-00897 | softener | [8 empty] | 100
continuos softener supply as following
1-max.flow :- 1m^3/hr-cationic resin sodium base
2-power supply 220V 30W 50HZ
02-06-00898 | Absolute filter | [8 empty] | 200
size:- 505mm X 504mm x 150mm
dop - test :- 990997%
02-06-00899 | cold room 3X2 meter | [8 empty] | 100
02-06-00900 | PC computer pantum I I I | [8 empty] | 100
02-06-00901 | particle detector | [7 empty] | 100
instrument used to test air purity by filters (HEPA filters)to assess quantity of particles present in certain volume of air
02-06-00902 | cold sterilizer | [7 empty] | 100
sterilizer metal and non-metal instruments as well as sophisticaled heat and moisture sensitive instruments using low temperature hydrogen - peroxide plasma sterilization technology. Dosnt degrade instruments no emissiion harmful to worlers
02-06-00903 | Table top dry hot air sterilizer | [7 empty] | 100
02-06-00904 | table top formation sterilizer | [7 empty] | 100
02-06-00905 | Atoclave poruos material 4ft3 | [7 empty] | 100
02-06-00906 | Plastic seeling machinc (with several role niylon) | [7 empty] | 8for equipment and (500) for rolles
02-06-00907 | 0.6 /1.2 kv single core cables , with flexible stranded circular copper conductors ,PVC .insulated and PCV sheathed
| Nomial cross section area mm2 | [7 empty] | Quantity
| 120 | [7 empty] | 20000 meter
| 240 | [7 empty] | 400000 meter
| 300 | [7 empty] | 120000 meter
| 3x50 +25 | [7 empty] | 60000 meter
02-06-00908 | Multy core cables , with flexible stranded copper conductor ,PVC insulated and PVC sheathed
| no. of cond.x cross section area | [7 empty] | Quantity (meters)
| 2x1.5 | [7 empty] | 20000
| 2x2.5 | [7 empty] | 20000
| 2x4 | [7 empty] | 10000
| 2x6 | [7 empty] | 6000
| 4x2.5 | [7 empty] | 10000
| 4x4 | [7 empty] | 20000
| 4x6 | [7 empty] | 4000
| 4x10 | [7 empty] | 4000
| 4x16 | [7 empty] | 4000
| 4x25 | [7 empty] | 4000
| 4x35 | [7 empty] | 4000
| 3x1.5 | [7 empty] | 4000
| 3x2.5 | [7 empty] | 4000
| 3x4 | [7 empty] | 4000
| 3x50 +25 | [7 empty] | 4000
| 3x70 +35 | [7 empty] | 4000
| 3x95 +50 | [7 empty] | 4000
| 3x120 +70 | [7 empty] | 4000
| 3x150 +70 | [7 empty] | 4000
| 3x185 +95 | [7 empty] | 4000
| 3x240 +120 | [7 empty] | 4000
| 3x300+150 | [7 empty] | 4000
02-06-00909 | Multicore cables with stranded copper conductors PVC insulated , steel wire armound and PVC sheathed
| 3x35 +16 | [7 empty] | 4000
| 3x50 +25 | [7 empty] | 4000
| 3x70 +35 | [7 empty] | 10000
| 3x95 +50 | [7 empty] | 4000
| 3x150 +70 | [7 empty] | 4000
| 3x185 +95 | [7 empty] | 4000
| 3x240 +120 | [7 empty] | 4000
| 3x300 +150 | [7 empty] | 4000
02-06-00910 | Cable terminals for cable sizes from 10 mm^2 to 300 mm^2 | [7 empty] | 2000PIECES FOR EACH SIZE
02-06-00911 | ELECTRICAL -HYDROLIC TERMINAL PRESS MACHINE | [7 empty] | 100
02-06-00912 | MANUAL - HYDROLIC TERMINAL PRESS MACHINE | [7 empty] | 100
02-06-00913 | EQUIPPED MOBILE LAB. FOR OCCUPATIONAL HEALTH AND SAFETY | [7 empty] | 100
02-06-0914 | EQUIPPED MOBILE LAB. Containing (noise level analyzer vibration analyzer ,condenser microphone ,triple microphone stand holder ,alpha numeric printer ,car counter ,electric generator ) | [7 empty] | 100
02-06-00915 | DO for cheking(BOD) , (ultra-dometer)
| instrument for determination of quantity of the mount of biological oxygen in water supplyment | [7 empty] | 100
extracts . Service system
02-06-00916 | electric refrigerator | [7 empty] | 100
02-06-00917 | kerosen refrigerator | [7 empty] | 100
02-06-00918 | vedio casset + CD | [7 empty] | 100
02-06-00919 | colour televsion (size : 24 note ) | [7 empty] | 100
02-06-00920 | telephone instrument | [7 empty] | 100
02-06-00921 | refregerated centrifuge | [7 empty] | 100
02-06-00922 | refregerated /heating water circulater (-10 TO 100 C) | [7 empty] | 100
02-06-00923 | freezer (-70) | [7 empty] | 100
02-06-00924 | refrigerator | [7 empty] | 100
02-06-00925 | microbiological safety cabinet and chemical hood and laminar air flow cabinet | [7 empty] | 100
02-06-00926 | phto copy machine | [7 empty] | 100
02-06-00927 | cuntarl station computer | [7 empty] | 100
| & terminal | [7 empty] | 100
02-06-00928 | cold room | [7 empty] | 100
02-06-00929 | office operatar with 100 lines | [7 empty] | 100
02-06-00930 | power amplifier (100W) | [7 empty] | 100units
model :- lbb 1103 (phillips)
02-06-00931 | air compressor | [7 empty] | 100
small for aeration of water sample (1-SL) sample valume
02-06-00932 | liquid nitrogen container of medium size (20 litres capacity) | [7 empty] | 100
02-06-00933 | softener
saadam medical city
| max flow:-90m^3/hr | [7 empty] | 100
| max flow:-70m^3/hr | [7 empty] | 100
| max flow:-50m^3/hr | [7 empty] | 100
general softener specification
dual/duplex system
resin:-strong cation
pressure vessel:high quality mild steel B.S 5500 working press 6 bar, internally protected by epoxy paint, eith manhole at tap.
valve:- amain multiport valve ,manual and automatic opreration
brine tank:-poly then with stainer and loose fit couer
operation:- flow counter supplied to intiat regeneration cycles
piping :- all piping including salt injeotion tubing is supplied
design row water condition
| total hardness |  | 289 to 610 PPM
| calcium |  | 84 to 323 PPM
| magnesium |  | 205 to 287 PPM
| other catios |  | 263 to 675 PPM
| bicar bonates |  | 160 to 159 PPM
| chlorides |  | 19 to 159 PPM
| totanions |  | 263 to 675 PPM
| chlorin |  | 1 to 2 cl PPM
02-06-00934 | ELECTRICAL OPERATED DOORS | [7 empty] | 28 nos
1-electric doors shall be of the type sually useel in hos pitals.
2-each door shall be supplied and operated by push button.
each two double doors to be electrically inter - locked.
NO. 8-groups each group
(2)double doors
(5) groups for ntrance the operation the consist at electrically inter - lock push button system doors with (1.8)mm vision stanless steel panel (2-phase) and for two type
1-5 double doors opening into scup - up withou freme and without glass ints size (1.80 x 2.3)
2-5 double doors opening into operation theater
(2) double glass close winelows door size (1.80 ) with 2.0mm stanless steel frame powder coat (for frame only) with same couloral op theater
(3)groups for entrance the operation zone each group (2) electrically inter lock push button with (1.8)mm stanless steel
(2-phase) - powder coateel and the coulor will be fixeed latter and each double door with (2) double glass windows without door frame and with size (1.80 x 2.35)MR the oratical size
No. (2)double doors with single lect.push button doors with (1.8)mm stanless steel panel (2-phase) powder coated its coulor will bre main sheel latter and its sizes (1.80 x 2.35)MR
No. (5) mechanicall single doors (1.0 x 2.10)MR with (1.8)mm stanless steel (2-phase) powder caoted with (2.0)mm stanless stel frome POW. Caoted sam caoted op. Theater
door mechanisnm shall be heaney duty mainterance free
aech door shall be locked when it is not in use
all inters al other services (elec, Hine mechan, soket , caoted coulor , bxass) to be considereel and installed all samples and detailes to be submitted for opproual before make it
all dimensions of the are taken from outer to outer door frame dimensions (wide and heiqht) and neet in sid elear span
air handling unit (AHU)
| type of filter | power (KW) | No.of motor | type of (AUH) |  | coucetion size (in-out)foreach coil |  | air-flow |  | water flow lit/min |  | water temp (in-temp)c |  | capacity KCA/h | qty.
|  |  |  | other type | in - line |  |  | for cooling | for heating | for cooling | for heating | for cooling | for heating
02-06-00935 | 2-no.meta- lic washable 50mm thiek 35%&bag 90% | 9 | 1 | _ | in-line mane | _ |  | 8500 | 8500 | 151 | 44 | 7.2 12.7 | 71.4 82.2 | 50330 | 10
02-06-00936 | 2-no.meta- lic washable 50mm thiek 35%&bag 90% | 10 | 2 | _ | in-line mane | _ |  | 10650 | 10650 | 245 | 91 | 7.2 12.7 | 71.4 82.2 | 80900 | 10
02-06-00937 | 2-no.meta- lic washable 50mm thiek 35%&bag 90% | 4 | 2 | _ | in-line single zone | _ |  | 2000 | 2000 | 58 | 22 | 7.2 12.7 | 71.4 82.2 | 19150 | 10
02-06-00938 | 2-no metalic washable thich middle effic. F 35% of hepa. F 99.77% | 13 | 2 | _ | in-lne malti zone | _ |  | 8500 | 8500 | 130 | 42 | 7.2 12.7 | 71.4 82.2 | 43050 | 10
02-06-00939 | 2-no.meta- lic washable type 50mm thich middle effici-f 35% & bag fill 90% effieic | 15 | 1 | _ | single zone | _ |  | 23370 | 23370 | 377 | 133 | 7.2 12.7 | 71.4 82.2 | 125500 | 10
02-06-00940 | 2-no.meta- lic washable type 50mm thich middle effici-f 35% & bag fill 90% effieic | 25 | 1 | _ | single zone | _ |  | 32790 | 32790 | 477.4 | 150.6 | 7.2 12.7 | 71.4 82.2 | 158940 | 10
02-06-00941 | requirements for simplex
| mobile radio system | [5 empty] | 100
mobile radio system compising the following main items is required to serve A service organization:-
1-two base station with dispatcher council to communicate with mobile and fixed station within 30 KM radius.(one to be used as spare unit).
2. High gain omni - directional antenna and feeder cable (100m) for the base station with the mask and all accessories.
3-10 fixed transceivers with directional antennas feeders and all others necessary accessories
4- 10 mobile vehicular transceivers with antennas feeders and all neccary accessories.
5-15hand uniys with necessary chargers and accessories
6-soare parts with avalue of 10% the total cost of equipment.
7-power supplie for the station and fixed units with U.P.S.
8-appropaiate test eqouipment>
9-full installation of the equipment should be part of the pffer and local training during installation.
10-on job trining should be offered
11-the frequency of operation will be allocated in the VHF frequency band (148-174MHZ).
12-the base sattion tx power should be between 10 and 25 watts and likewise for the fixed and mobile units. The handheld tx power should be between 3-5 watts.
13-warrenty one year from date of operation .
14-two years maintenance after period of warrenty.
15-training operaters and technicl staff on factory.
16- 2-complete sets of diagrams and manuals
| ype |  |  | head m | capasity L/min |  | suction m m |  | P(KW) |  | QTY
02-06-00942 | sewage submersible pump | _ |  | 22m | 400L/min |  | discharge 100 mm |  | 7.5KW | discharge | 10
02-06-00943 | water pump for sanitory HP2 | vertical |  | 15m | 50L/min |  | suction 32m m |  | 0.75KW | _ | 10
02-06-00944 | water pump for sanitory HP3 | vertical |  | 20m | 100L/min |  | suction 40m m |  | 1.5kw | _ | 10
02-06-00945 | chemical dosing pump for cooling tower | vertical |  | _ | 10kg/cm2 110cc/min |  | suction 2inch |  | 30watt | r.p.m= 1300 | 10
02-06-00946 | circulating water pump HP | vertical |  | 29.7m | 320 L/m |  | _ |  | 2.2 | r.p.m=1470 | 10
02-06-00947 | submersibte pump SP | _ |  | 10m | 1000L/m |  | 100 mm |  | 3.7 | r.p.m= 1500 | 10
02-06-00948 | eng camera
| item No. | descrription |  |  |  |  | quantity (state unit)
| 1 | betacam sp camcorder camera PVW-D 30 PF |  |  |  |  | 500
| 2 | play back adaptor VA-300P |  |  |  |  | 500
| 3 | rechargable NI - CD battery |  |  |  |  | 500
| 4 | AC adapter AC - 550 CE |  |  |  |  | 500
| 5 | battry case DC - 520 |  |  |  |  | 500
| 6 | chest pad CAC - 4 |  |  |  |  | 500
| 7 | microphone holder CAC 12 |  |  |  |  | 500
| 8 | battry charger BC - 1 wdce |  |  |  |  | 500
| 9 | UHF wireless microphone wrt - 830 a with UHF wirless receiver (complete) |  |  |  |  | 500
| 10 | betacam sp 20 min. metaltape |  |  |  |  | 500
| 11 | betacam SP 30 min. metaltape |  |  |  |  | 500
| 12 | tripod - vision 10 lf complete set |  |  |  |  | 500
02-06-00949 | A/B roll editing system with DFS - 500 P (digital effects)
| item No. | complete description of item |  |  |  |  | quantity (state unit)
| 1 | betacam sp recorder |  |  |  |  | 100
| 2 | betacam sp player |  |  |  |  | 100
| 3 | editing control unit |  |  |  |  | 100
| 4 | vtr interf ace |  |  |  |  | 100
| 5 | serial switche interf ACE |  |  |  |  | 100
| 6 | B/W data display |  |  |  |  | 100
| 7 | bme switcher |  |  |  |  | 100
| 8 | serial switche interf ACE |  |  |  |  | 100
| 9 | color monitor |  |  |  |  | 100
| 10 | color monitor |  |  |  |  | 100
| 11 | dubbing cable (12 pin) |  |  |  |  | 100
| 12 | remote control cable |  |  |  |  | 100
| 13 | audio mixer |  |  |  |  | 100
| 14 | audio amplifire |  |  |  |  | 100
| 15 | speaker (3 WAY) |  |  |  |  | pair
| 16 | desk & pack mount metal |  |  |  |  | complete
| 17 | main power output with AC out let box |  |  |  |  | 100
| 18 | bet acam sp plater |  |  |  |  | 100
02-06-00950 | cold stor | [5 empty] | 100
internal temp. raning form (-20c) to (+10C) at the folowing amdient conditions
summer : DBT 45C
winter : DBT _ 5C
internal volum not less than 32 cubic meters
referigeration system two indepent refrigeration with an automatic altermatorm clock timer furnished to automatically reverse the sequence of operation of the two systems , and if one system be unable for any reason to maintain the required temp. the second system shall automatically cut in
system shall operate from single - phase 220V , 50HZ or 3phase , 4wire 380v
02-06-00951 | AMBULANCE | [5 empty] | 1000
PARTITION
BETWEEN DRIVER'S COMPARTMENT AND PATIENT’S COMPARTMENT FULL COVERAGE PANEL MADE OF STURDY MATERIAL (PRESS WOOD IS NOT TO BE USED) WITH SMOOTH SURFACE AT BOTH SIDE.
PARTITION WINDOW
LARGE, DOUBLE SLIDING SAFETY GLASS CENTRAL WINDOW
PATIENT'S COMPARTMENT
THE PATIENT'S COMPARTMENT IS TO BE FULLY INSULATED.
ROOF HEIGHT
INSIDE HEIGHT NOT LESS THAN 1500MM WITHOUT THE THICKNESS AND REINFORCEMENT.
FLOORING
HIGH QUALITY FLOORING MATERIAL CEMENTED TO A SUITABLE TYPE OF WOOD WITH ALUMINUM MOLDING.
MEDICINE CABINETS
THE LEFT WALL OF THE PATIENT’S COMPARTMENT IS TO BE PARTITIONED INTO ENCLOSED STORAGE CABINETRY. COMPARTMENT SPACE AND SHELF SPACE TO BE CONVENIENTLY LOCATED FOR MEDICAL SUPPLIES, DEVICES AND INSTALLED SYSTEM AD APPLICABLE FOR THE SERVICE INTENDED. CABINETS ARE TO BE EASILY OPENED WITH SHATTERED-PROOF TRANSPARENT SLIDING DOOR THE WALL IS TO BE NOT MORE THAN 30 INCHES HIGH. REMOVAL OF CABINET IS TO BE EASY TO FACILITATE BODY REPAIR IN CASE OF AN ACCIDENT.
TECHNICIAN SEAT - FRONT
PROVISION OF A TECHNICIAN SEAT AT THE FRONT OF THE PATIENT'S COMPARTMENT.
TECHNICIAN SEAT-REAR
PROVISION OF A TECHNICIAN SEAT AT THE FOOT OF THE PATIENT'S ON THE RIGHT END SIDE.
INSIDE LIGHTING SYSTEM
THE PATIENT'S COMPARTMENT ELECTRICAL SYSTEM IS TO BE SEPARATED FROM THE TRUCK.
IDENTIFICATION
THE AMBULANCE IS TO BE IDENTIFIED AS FOLLOWS:-
IT IS TO BE PAINTED CLEAR WHITE
- FOR DECALS FOR THE WORD "AMBULANCE", AND A RED CRESCENT IN ARABIC ONE ON EACH SIDE, ONE ON THE REAR, AND ONE ON THE FRONT
RESUSCITATION EQUIPMENT
- TWO OXYGEN BOTTLES, EACH OF 500 LITTER CAPACITY SECURED WITHIN THE LEFT WALL CABINETRY.
- TWO SPARE OXYGEN BOTTLES OF 500 LITTER CAPACITY IN STOWAGE CABIN.
- ONE SET OF ENGLISH BULL NOSE VALVE YOKE, PRESSURE REGULATOR WITH GAUGE FLOW METER AND HUMIDIFIER BOTTLE.
- THREE OXYGEN MASKS, ONE FOR EACH ADULT CHILD AND INFANT.
- THREE PLASTIC NASAL CANNULAS, TWO ADULT AND ONE CHILD.
- FOUR OXYGEN CATHETERS, TWO OF EACH NO.10F.
ONE MOUTH TO MOUTH VENTILATION MASK
| CYLINDER KEY | [5 empty] | 1 FOR EACH
| OXYGEN FLOW METER /REGULATOR | [5 empty] | 1 FOR EACH
| HUMIDIFIER | [5 empty] | 1 FOR EACH
PORTABLE OXYGEN KIT
ONE PORTABLE OXYGEN KIT COMPETE WITH REGULATOR AND SUPPLIES.
| RESUSCITATOR COMPLETE WITH CYLINDER. | [5 empty] | 1 FOR EACH
| RESTRAINING STRAP FOR RESUSCITATOR. | [5 empty] | 1 FOR EACH
SUCTION SYSTEM
ONE VACUUM APPARATUS INCLUDING AN ELECTRIC DRIVEN PUMP with rechargable battery
FIRST AID EQUIPMENT
A BOX IS TO BE PROVIDED CONTAINING THE FOLLOWING:-
TWENTY PRE- LOCALIZED PADS
TWELVE COMPRESSIVE BANDAGES
- FOUR 10CM ELASTIC STRIPS.
- SIX GAUZE BANDEAUS, THREE OF 75MM AND THREE OF 150MM.
- TWENTY GAUZE PADS 10CM BY 10CM, INDIVIDUALLY WRAPPED.
- TWO 5CM ANTI-ALLERGIC ROLLS OF ADHESIVE TAPE.
FIFTEEN TONGUE DEPRESSORS INDIVIDUALLY WRAPPED.
- ONE 100 ML BOTTLE CONTAINING CHLOREXIDINE BASE DISINFECTANT.
AIR SPLINTS
ONE SET OF AIR SPLINT FOR EACH OF THE UPPER AND lower LIMBS.
STRETCHER
WHEEL STRETCHER WITH ADJUSTABLE BACK AND FOOT RESTS WITH SIDE HANDLES, COMPLETE WITH MATTRESS AND COVER.
SPARE STRETCHER
FOLDING COLLAPSIBLE STRETCHER WITH SUPPORTING SPREADER BARS AND VINYL COATED NYLON FABRIC.
REAR BUMPER STEP
A- REAR BUMPER STEP IS TO BE INSTALLED OVER THE REAR BUMPER.
BOTTLE HOOKS
BOTTLE HOOKS ARE TO BE INSTALLED ON THE ROOF TO HOLD FLUID AND BLOOD TRANSFUSION BOTTLES.
SPARE STRETCHER HOLDER
SPECIAL HOOKS ON WALL AND ROOF ARE TO BE PROVIDED TO HOLD SPARE STRETCHER WHEN REQUIRED.
EXHAUST-VENTILATOR FAN
ROOF MOUNTED DOUBLE ACTING EXH-VENT FAN IS TO BE INSTALLED.
REAR BUMPER STEP
A REAR BUMPER STEP IS TO BE INSTALLED OVER THE REAR BUMPER.
BOTTLE HOOKS
BOTTLE HOOKS ARE TO BE INSTALLED ON THE ROOF TO HOLD FLUID AND BLOOD TRANSFUSION BOTTLES .
ANTENNA
INSTALLATION OF RADIO ANTENNA IN EACH AMBULANCE AT THE ROOF.
WIRELESS EQUIPMENT: EACH AMBULANCE EQUIPPED WITH RADIO (WIRELESS COMMUNICATION DEVICE).
SPECIFICATIONS FOR AMBULANCES
BASIC VEHICLE
ENGINE: PETROL ENGINE WATER COOLED .
TRANSMISSION: MANUAL OR AUTOMATIC.
AXLE: 4X4 wheel driver
STEERING :POWER STEERING LEFT HAND DRIVE.
SUSPENSION : HEAVY DUTY.
COOLING SYSTEM: HEAVY DUTY.
ELECTRICAL SYSTEM: 12 VOLTS WITH HEAVY DUTY ALTERNATOR AND BATTERY.
AIR CONDITIONING SYSTEM: AIR-CONDITIONER AND HEATER FOR BOTH DRIVER AND PATIENT COMPARTMENTS.
SIDE DOOR: SIDE DOOR AT THE RIGHT SIDE.
BACK DOORS: TWO PANEL DOORS OPENABLE TO THE SIDES.
INSTRUMENT PANEL: WITH METRIC GAUGES and ODOMETER.
MIRRORS: ONE INSIDE and TWO OUTSIDE REAR VIEW.
TIRES :HIGH QUALITY INCLUDING SPARE.
-WARNING EQUIPMENT: SIREN WITH SPEAKER AND BEACON OF THE FOLLOWING TYPES:
-ELECTRONIC SIREN WITH PUBLIC ADDRESS SYSTEM OF 100WATTS OUT-PUT POWER.
BEACON : TWO REVOLVING DOME TYPE BEACONS LONGITUDINAL A LONG THE WIDTH ON THE FRONT ROOF
-SPEAKER: 100 WATTS SPEAKER INSTALLED INSIDE ENGINE COMPARTMENT.
-ACCESSORIES:
AUTO JACK WITH HANDLE and WHEEL WRENCH.
TOOL KIT BAG.
HAZARD WARNING TRIANGLE
FIRE EXTINGUISHER.
-MISCELLANEOUS: THE FOLLOWING IS TO BE SUBMITTED TWO WEEKS AFTER ORDER CONFIGURATION:
-WORKSHOP MANUALS (2 COPIES IN ENGLISH).
-SPARE PARTS CATALOGUES (2 COPIES IN ENGLISH).
-RECOMMENDED SPARE PARTS LIST (DETAILS OF THE LIST ARE TO BE AGREED UPON).
FAST MOVING PARTS for EACH VEHICLE.
- TRAINING FOR 3 ENGINEERS.
optional rquipments schedule ambulance
| VACUUM MATTERS WITH CARRYING HANDLES. | [5 empty] | 1 FOR EACH
| PUMP FOR VACUUM MATTRESS | [5 empty] | 1 FOR EACH
| FOLDING STRETCHER | [5 empty] | 1 FOR EACH
| INFLATABLE SPLINTS, SET OF 4 IN WALLET. | [5 empty] | 1 FOR EACH
| ANALGESIC UNIT. | [5 empty] | 1 FOR EACH
| NITRONOX CYLINDER (LIGHT WEIGHT) | [5 empty] | 1 FOR EACH
| URINAL, MALE. | [5 empty] | 1 FOR EACH
| URINAL, FEMALE. | [5 empty] | 1 FOR EACH
| ORTHOPEDIC SCOOP STRETCHER | [5 empty] | 1 FOR EACH
| BRACKETS FOR SCOOP STRETCHER. | [5 empty] | 1 FOR EACH
| HEAPED AND HARDNESS SET FOR SCOOP STRETCHER. | [5 empty] | 1 FOR EACH
| ASPIRATOR, MANUAL | [5 empty] | 1 FOR EACH
| AMBULANCE CHAIR | [5 empty] | 1 FOR EACH
| BRACKET FOR AMBULANCE CHAIR | [5 empty] | 1 FOR EACH
| FIRST AID KIT COMPLETE WITH CASE. | [5 empty] | 1 FOR EACH
| PENLIGHT | [5 empty] | 1 FOR EACH
| BEDPAN | [5 empty] | 1 FOR EACH
| ANEROID SPHYGMOMANOMETER | [5 empty] | 2 FOR EACH
| STETHOSCOPE. | [5 empty] | 2 FOR EACH
| OTOSCOPE. | [5 empty] | 1 FOR EACH
| THOUGHT CUT SCISSORS. | [5 empty] | 1 FOR EACH
| SEMI AUTOMATIC DEFIBRILLATOR /MONITOR | [5 empty] | 1 FOR EACH
| SECURING DEVICE FOR DEFIBRILLATOR /MONITOR | [5 empty] | 1 FOR EACH
| ARTERY FORCEPS (SPENCER WELLS) | [5 empty] | 1 FOR EACH
| DISSECTING FORCEPS, PLAIN | [5 empty] | 1 FOR EACH
| SCISSORS BANDAGE. | [5 empty] | 1 FOR EACH
| THERMOMETER | [5 empty] | 1 FOR EACH
| NON WOVEN ACRYLIC BLANKET 60"X80" APPROX. | [5 empty] | 1 FOR EACH
| CELLAR BLANKET UNBLEACHED 60"X80" APPROX. | [5 empty] | 2 FOR EACH
| FOAM PILLOW, PCV COVERED | [5 empty] | 2 FOR EACH
| VACUUM FLASK STAINLESS STEEL 1 LITTER. | [5 empty] | 2 FOR EACH
| RESTRAINING STRAP FOR VACUUM FLASKS | [5 empty] | 1 FOR EACH
| OXYGEN CYLINDER, BULL NOSE (SIZE F) | [5 empty] | 1 FOR EACH
| OXYGEN FACE MASK | [5 empty] | 1 FOR EACH
| GREEN BUBBLE 30 FOOT ROLL | [5 empty] | 2 FOR EACH
02-06-00952 | freezer -80 | [5 empty] | 100
1-horzintal type heavy insulation or vertical type
2-temp . Range 0 - (-80c)
3-double compressor heavy duty with fan cooling system
4-alarm - system
5-thermal - control - system with multi - indicators
6-parttion and baskets for samples
7-size 16-20 cubic feet
02-06-00953 | freezer -20 | [5 empty] | 100
1-horzintal type heavy insulation or vertical type
2-temp . Range 0 - (-80c)
3-single compressor heavy duty with fan cooling system
4-alarm - system
5-thermal - control - system with multi - indicators
6-parttion and baskets for samples
7-size 16-20 cubic feet
02-06-00954 | lab - refrigrator | [5 empty] | 100
1-14cupic feet type with lock for freezing & refrigrater
2- double door one for freezer ( - 10c) & one for refrigrater (4 - 8c )
3- freezer :- parttions 2 or 3 with drawers for freezing samples ( _10c)
4-refrigrater (4 - 8c) with parttions (4 - 5) and drawer supplied with (D R I N) out let for washing and sterlization
5- heavy duty compressor with fan for cooling purposes
6-refergerater and freez have thermometer fixed on the front side
7- refrigerater have atomatic defrost system
8-220v/50HZ/ 1 PH
9- R134
02-06-00955 | blood bank coold store | [5 empty] | 100
inside temp from 1C to 6C at the following ambient conditions
summer : DBT 50 C
WBT 25 C
winter : DBT 1C
WBT -3 C
Internal volume : not less than 50 cubic meters
A) construct ion :
1- cold stores shall be shipped in knock – down sections to re-erect
2- cabinet interior shall be made of heavy corrosion proof aluminum, floor made of heavy gauge anti – slip aluminum
3- cabinet exterior shall be made of aluminum , coated with a white weather proof coating to make it suitable for out-door installation
4-In sultan shall be sufficient to maintain the specified internal temperature in the specified ambient condition but shall be not less than 10 cm of polyurethane
5- Door shall be constructed of aluminum & shall have an external lock with keys. Door handle can be operated from inside & outside. Low voltage heater wire strip with electrical control shall be provided. Apish-button shall be fitted inside to sound an alarm in case of person is trapped
6- light- weight shade to protect the cabinet from rain & sun to be fitted on top of it. Shape size & material of shade shall be suggested by the tendered
7- external dial thermometer must be provided
8- Audio & visual alarm for high temperature must be fitted
9- Sufficient internal lighting automatically switches on when door opens
10- air curtain by the door operates automatically when door opens
11- Shelves shall be made of strong galvanized steel positioned on all sides shelves shall be grid type accommodating heavy blood bank refrigerator drawers full of blood pints when stored in the cold room and carried to or from it 3 raws of shelves
12- (7 days recorder
B) .REFRIGERATION SYSTEM
Two independent refrigeration system shall be installed each being capable to maintain the required internal temp. at the specified ambient conditions an automatic alternator clock timer shall be furnished to automatically reverse the sequence of operation of the two systems to assure even wear , and if one system be unable for any reason to maintain the required temp. the second system shall automatically cut- in . Visual indication of the operation & faults of the system shall be shown on the control panel. Capacity &type of compressor used shall be mentioned in the offer . the entire system shall utilize heavy duty refrigeration copper tubing , no aluminitium or steel tubing to be used . evaporator fins shall be anticorrosion type . automatic electrical defrost with pipes for drain water must provided .use R12 or R502
C) Electrical system
System shall operate from single – phase , 220V, 50 HZ, supply or from 3 pH , 4 wire , 380 V
D) Spar parts 5 years
02-06-00956 | Developed operating washing tube | [5 empty] | 100
02-06-00957 | PIIII or PIII with accessires and read - write CD - drive | [5 empty] | 100
| printer EPSON LQ - 2180 | [5 empty] | 100
| laser - printer 10 L | [5 empty] | 100
| page printer | [5 empty] | 100
| U.P.S | [5 empty] | 100
| reglater power 10AMP | [5 empty] | 100
| reglater power 20AMP | [5 empty] | 100
| white board | [5 empty] | 100
| over head pros | [5 empty] | 100
| sidlater | [5 empty] | 100
| disk 3.5 | [5 empty] | 500
| laser - disk | [5 empty] | 100
02-06-00958 | intercom system
| central digital intercom system comprise of one master station with special faeilities and 100 or 50 slave station, the system evakle each slave station to communicall with other slave station and with the master station |  |  |  |  | 60 for system with 50 slave station
| _ installation the systems on siltes |  |  |  |  | 200 for system with 100 slane stations
_ one year earranty and two year maintenaes
_ complete sets of drawing and manuel and catalogues
_ spetionl too kit for each system
_ training coerse 4 engineers for 3 weeks , on factory
_ spare parts for two years
02-06-00959 | clock system | [5 empty] | 500
| central clock system contoins:- | [5 empty] | 500
| a- master clock | [5 empty] | 500
| b- single face slave clock | [5 empty] | 500
| c- double face slave clock | [5 empty] | 500
| d- special clock for operating theater | [5 empty] | 500
| c-time machine | [5 empty] | 500
one year waranty , two year maintenaes, installation complet set of manuals and catalogies and drawing spare parts for two years
training coerse on factory for 3 engineers for 3 weeks
02-06-00960 | electrical switchs and souket
| 1-single switch 220V /up to 15A - B.5 | [5 empty] | 50000
| 2-double switch 220V / up to 15 A - B.5 | [5 empty] | 50000
| 3-frible switch 220V / up to 15 A - B.5 | [5 empty] | 50000
| 4-four way switch 220V / up to 15 A - B.5 | [5 empty] | 50000
| 5- mercury switch 220V / up to 15 A - B.5 | [5 empty] | 50000
| 6- electrecal out let 220220V / up to 13 A - B.5 13A - B.S | [5 empty] | 50000
| 7- electrecal out let 220220V / up to 15 A - B.5 13A - B.S | [5 empty] | 50000
02-06-00961 | over loads
| NO. of poles | NO. of phaes | current A | Voltage | Qty
| 3P | 3Q | 0 - 35 | 220V | 2000
| 3P | 3Q | 5 40 | 220V | 2000
| 3P | 3Q | 3 60 | 380V | 2000
| 3P | 3Q | 80 -200 | 380V | 2000
| 3P | 3Q | 30 - 90 | 380V | 2000
| 3P | 3Q | 20 - 80 | 380V | 2000
| 3P | 3Q | 2 15 | 380V | 2000
| 3P | 3Q | 200-500 |  | 2000
02-06-00962 | contactors
| NO. of poles | NO. of phaes | No. of auxiliang contact | Voltage of coil | Voltage | current A |  | Qty
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 10A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 16A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 20A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 25A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 30A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 40A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 50A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 60A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 80A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 100A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 250A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 400A |  | 1000
| 10 | 3Q | 4 (2no , 2nc) | 220V | 400V | 1000A |  | 1000
02-06-00963 | automatic sliver recofery | [6 empty] | 1000
power 220v , 50hz single phase
capacity (20liter - 40liter)
not more or less than
02-06-00964 | sound and interpretation system | [6 empty] | 500
a simulaneous interpretation system in auditorium uses lectroacoustic equipment to bring an immediate translation of 4 foreign language and thirth floor language each member being provided with the means of sketching the language of their choice.
the equipment shall be suitable for operation in baghdad under temperatures ranging from 0C to 50C and relative humidity of up to 70%
thebasic constituents of the system:-
1-central control desk
the central control desk which controls the 232 conference and interpreters microphones,has been specially designed for ease of operation.housed in an attractive metal/teak housing the desk will fit in with the most demanding standards of conference room interior design. although it is generally supervised by a control operator , for smaller installations the chairman could perform this function himself.
each language channel is equipped with asound level meter and an indeqendent volume control. These enable the controller to accurately balance the difference in speech levels of the interpreters voices. The desk incorporates the following controls for ease of operation:-
A- 4 VU meters for checking the sound level of each of the 4 translation channels separately.
B-4volume controls for adjusting the sound level of each of these channels individually.
C-one VU meter for checking the sound level of the floor language plus one volume control adjusting the sound level. Tow language selectors.
D-one monitor loudspeaker.
E- 4 volume controls.
F-one headphone socket for monitoring.
G-4 push - buttons for signals to the interpreters
H-4 pilot - lamps for signals from the interpreters
the 5 VU meters provide avisual check and the headphones an aural check of the sound intensities on the 5 channels . The push - button and pilot lamps correspond with the pilot lamps and push buttons on the interpreters desks.
the 5 volume controis situated underneath the VU meters enable the operator to avoid too large a variation in voice level between different speakers
connections for tape recorders are available.
2-chairman s microphone
this is the only microphone , which is not centrally controlled and the only one with which it is possible to cut on a speaker the chaimans microphone is provided with a priority switch that allows to him break in on any speech . This is particularly usful should he wish to question to clarify points raised by a speaker or to call the meeting to order . during his interruption , the chairman may switch the speakers microphone off or leave it on whichever the chooses
the chairman s microphone unit is acardoid microphone with gooseneck located on a stand , which incorporates an on/off button and a priority button , both withpilot lamps.the on/off button allows the chairman to switch his microphone on or off without affecting the speakers.
microphone , e.g. when he wants to participate in a discussion. The priority button switches on the chairmans own microphone and at the same time switches off all speakers microphones (but not the interpreters microphones).
3-interpreters booths
A sound - proof booth is required for eacg of the languages begin interpreter . Here the interpreter can monitor speech throgh headphones and relay an immediate translation into his microphone with minimum of distracting ambient noise.
an interpreters microphone unit is designed for installation in interpreter s booths the unit is designed for use by 4 interpreters working simultaneously or alternatively.
this is because in most conferences the proceedings often continue for longer periods than one interpreter can work for . Thus this unit is fitted with tow sets of controls , inputs and out puts.
4 rotary - type switches enable the interpreter to select either the floor language , or one of the 4 translation channels, and separate level controls , and provided for each of the headset out puts.
the microphones are controlled by separate keys : the circuit begin so arrang that with both keys in the off position the floor language is automatically relayed to the interpreters channel.
the remaining desk unit controls are asingle push - button and lamp for signaling to and from the central control desk.
each interpreter has a standard microphone unit a pilot lamp mounted on the base of the microphone unit serves to indicate that the microphone is switched on and a mute button is provided to allow temporary switch out of the microphone .
the desk unit is of study all - metal construction with a pleasing funetional design .
installation connections are simply and quickly made by means of one multi - core flexible cable and connection box.
4-monitoring units
the monitoring unit and light-weight headphones enable those attending the conference to listen in to any one of the 4 simultaneous interpretations each unit possesses a language selector avolume control and headphone out put socket . Monitoring units must be for the cabled transmission system.
bill of quantities
supply install and test following outlet points by means of cable indicated on the sraeings (from the central control desk with amplifier unit) enclosed in heavy gauge galvanized steel conduit, cable trench including connections etc as required
supply install test and commission following equipment as specifications ineluding connections as required.
A-chairmans unit with microphone and loudspeaker (table type) with suitable socket. 1 NO
B-delegates unit with as above. 60 NO. Chair type
C-interpreters unit with as above 4 NO. Table type
D-loud speakers (sound column type /2 watt of capacity) with suitable sockets 2NO.
suply install test and commission chair control unit as per specifications including connections as required
A-5 channels program selector. 1NO
B- miniature juck socket for headphone 1NO
C- light - weight stethophone
frequency response 100 - 4000HZ nominal power 1 mw max load 15 mw or any standard. 1NO
| D-microphone flush mounted in chair with on/off switch and with lamp indicator power supply 24V to 26V D.S frequency range 200 -14000 HZ 1NO. | [6 empty] | from A toD 232set
supply install test and commission central control desk with 12 input and 4 out put channels and amonitor channel as per specifications including connections as required
A-amplifier 50 watt. 1NO
B-operators microphone . 1NO
C-cassette recorder. 1NO
supply , install , test and commission following equipment as per drawing with suitable sockets and connections.
A-floor loudspeaker with volume control and on/off switch connecting to interpreters junction box. 4 NO
02-06-00965 | electric dryer | [6 empty] | 50
30KG
02-06-00966 | loundry press for clothes | [6 empty] | 50
1-electric
2-heater 1.2kw
3-running matorl (400W)
4-blower 65 W 220V , 50HZ
02-06-00967 | loundry extractor | [6 empty] | 50
30kw
02-06-00968 | computer | [6 empty] | 100
1-pentium III 550 MHZ 512KB cash
hard disk 10GB
H.D floppy disk drive (3.5)
cd - rom drive(52X)
ethermet card
512MB RAM
UPS (400VA)
sound card + speakers
| 2-multimedia projector :-brightness 800 ANSI lumener resolusion 800X600 | [6 empty] | 1
| 3-scanner :- optical resolution (at least 600 X 1200dpi) | [6 empty] | 1
| 4-laser printer :-A4 (at least 600 dpi X 600dpi resolution) | [6 empty] | 4
| 5- colour printer :- A3 color inkjet printer | [6 empty] | 1
| 6-CD - ROM writer:- CD RW 32 X4X4 SCI | [6 empty] | 1
02-06-00969 | BLOOD COMPONENT DEEP FREEZER
double compresser
capacity 26.232 fee^3
40.450fee^3
| type 0f freez :-5 vertical | [6 empty] | 100
| 5 horizntal | [6 empty] | 100
tem. :- 0 - 80C
02-06-00970 | electronic sphggmomanometer | [6 empty] | 100
02-06-00971 | cloth auto calve capacite 10 for sterilization surgical cloths | [6 empty] | 250
02-06-00972 | medical video recorder system type olympus for recording TV presentation for medical teaching and documentation purposes | [7 empty] | 250
02-06-00973 | Deep freezer
1-vertical type & modile
2-temperture :- from zero to minus 60C (D-60C)
3-capacity :-26cubic foot (f^3)
4-voltage :-220 volt
5-frequency :-50 HZ
6-compressor :-singh phase
7-spare compressor (s) to each main compressor (S) in the eych which act automatically in case of any defect or damage in the main compressor (S)
8-alarm system sensetive to any incremenf in the temperature beyond the desirabl degree
9-thermometer & temperture recorder fixed on the outer surface of the deep freezer
10- moving drawers alony rach of incorrosive stainless steel
11-the inner sarfaces of the deep freeaers showd be of in corrosive stainless steel
12-ttanble with lock a keye.
13-insulator of best quatity.
02-06-00974 | washer extractor 30KG | [7 empty] | 100
02-06-00975 | closed circuit TV | [7 empty] | 100
1-close circuit TV systems for microscopic projector
2-close circuit TV systems from the endoscopes to the lecture room
02-06-00976 | FREEZER | [7 empty] | 100
a-size 14 feet
b-six vertical and four horizontal
c-storage temperature (-20C)
02-06-00977 | FREEZER | [7 empty] | 100
a-size 16 feet
b-vertical type
c-storage temperature (-80C)
02-06-00978 | REFRIGERATOR | [7 empty] | 100
a-size 16 feet
b-vertical type
c-storage temperature (0-5)
02-06-00979 | INCINERATOR | [7 empty] | 100
A-size 1.0 X 1.5 meter
b-height 8 meters
02-06-00980 | telephone exchange | [7 empty] | 100
fuel a automatic
b-with 10 external lines and 60 internal lines . (each).
02-06-00981 | washing machine | [7 empty] | 100
a-heavy duty
b-size :-2(with washing capacity of 25 - 30 KG) and 1 (with washing capacity of 15 - 20KG)
02-06-00982 | BOILER | [7 empty] | 100
A-SMALL SIZE (OUT PUT CAPACITY 2250000 b.t.u/hrs) max. working pressure (65)psi
b-large size (out put capacity 3250000 b.t.u/hrs) max . Working pressure (65)psi
02-06-00983 | freezer | [7 empty] | 100
1-vertical type & modile
2-temperture :- from zero to minus 60C (D -60C)
3-capacity :-26cubic foot (f^3)
4-voltage :-220 volt
5-frequency :-50 HZ
6-compressor :-singh phase
7-spare compressor (s) to each main compressor (S) in the eych which act automatically in case of any defect or damage in the main compressor (S)
8-alarm system sensetive to any incremenf in the temperature beyond the desirabl degree
9-thermometer & temperture recorder fixed on the outer surface of the deep freezer
10- moving drawers alony rach of incorrosive stainless steel
11-the inner sarfaces of the deep freeaers showd be of in corrosive stainless steel
12-ttanble with lock a keye.
13-insulator of best quatity.
02-06-00984 | cold water storage pressed steel sectional tanks | [7 empty] | 200
1-dimensions of lower tank (7320 x 3660 x 3660)mm
dimensions of upper tank (6100 x 3660 x 1220)mm
2-diameters of in and out pipes should be as follows:-
lower tank
diam.of inlet pipe with flange and mechanical
type float (brass type) 100mmQ
diam. Of outlet pipe with flange 100mmQ
diam. Of over flow pipe with flange 100mmQ
diam. Of drain pipe with flange 100mmQ
diam . Of vent pipe with flange 50 mmQ
upper tank
same dimensions as above (but with out float mechanical float)
3-explaining the quantity of galvanization in gm/m^2
4-pipes with flanges for mlet , out let , draim , etc should be welded before galvanization
02-06-00985 | accident emergency ambulance | [7 empty] | 200
partition :-
between drivers compartment and patients compartment full coveroge panel made of sturdy material (press wood not to be used) with smooth surface at both side.
partition window:-
large double sliding safety glass window behind driver cabinet its height half inside height of roof height
patienty eompartment:-
the patienty compartment is to be fully insu - lated.
roof hight:-
in sid height more than 1850 mm. With out the thickness and rein fore ment.
flooring:
ttigh gnality flooring material cemented to a suitable type of wood with aluminum molding
identification:-
the ambulance is to be identified as follows:-
_ it is to be parted clear white.
for decal for the word (ambulance) and ared crescent in arabic one on each side one on the rear and one on the front
medicine cabinets:-
the left wall of the patients compartment is to be partition into enclosed storge capintry compartment space and shelf space to be conveniently located for medical supplies devices and installed system and opplicable for the service intended.
cabinets are to be easily opened with shattered - proof transpareent shding door the wall is to not more than (75)c.m high removel of cabinet is to be easy to facilitate bady repair in case of an accident.
technician seat - froni:
provision of atechnician seat at the front of the patients compartment.
technician seat -rear:
provioion of a techniecian seat at the foot of the pts on the right end side.
inlighting system:
the pts compartment slectrical system isto be separated from the truck.
resusciiaiion :
a-two oxygen bottes each of 1500 litter capaceity secured within the left wall calinetry.
b-two spare oxygen bottes of soo litter capacity in stowage cabin.
c-one set of english bull nose valve yoke pressere regulator with gauge flow meter anel humidifier bottle.
d-three size oxygen masks one for each adelt child and infant.
e-three plastic catheters two of each no. 10f.
f-one mouth to mouth ventilation mask
suciion system
one vacuum apparatw in cluding an electric driver pump (with rechargable battrey)
flrst and equipment:
abox is to be provided containing the following
1-twenty pre - localized pads
2-twelve compressive bargages
3-four 10 c.m elastic strips
4-six gamze bandge three of 75mm and three of 150m.m
first aid equipment:-
1-twnty ganze pads 10 cm by 10cm individ- ually wrpped.
2-two 5cm anti - allegic rolls of adhesive tape.
3-fifteen tonge depressors individually wrapped.
4-one 100 ml bottle containing chlorexidine base disintectanl
air splints
one set of air splint for each of the upper and limbs
three zise of extrication collar
ampu
three size of ambu (adult child aul intant)
stretcher
wheel hydrolic stretcher with adjustable back and foot rests with side handles complete with mattoress and cover.
spare stretcher
1-folding collapsible stretcher with supprting spreader bars and vinyl coated nylon fabric
2-spare stretcher holder : special hooks on the wall and roof are to be provided to hold spare stretcher when required.
3-aluminum orthopedic stretcher.
4-orthopedic scoop stretcher.
5-heaped and hardness set for scoop strecher
ambulance chair:-
with bracket (wold by special hooks on the back door)
rear bumper setp:
arear bumper step is to be intallel over the rear bumper.
bootle hooks:
bottle hook are to be installed on the both side of roof to hold fluid and blood transfusion bootls
pregnancy tools:
exhauzt - ventilator fan:
roof mounted double aeting exh - vent fan is to be installed.
projector:
exlernal projector over the outsid of drivers campartment turn by spesial handle in side of the cabinet.
external projeetors around the car and over the back doors open outomatic with its open.
stand - wash
steel done by foot.
semi automatic defibriliator/monitor
securing device :
for defidrillator/ monitor
aneroid - sphggmomanometer
stethscope
dissecting
artery forceps (spencer wells)
otoscope.
2-non woven acrilic blankcel (60x80)apporay.
2-cellar blanket undleached (60x80) apporax
2-foam pillow pcv covered
penlight.
optional equipmens shedule
ambulance
vacuum matters with carring handles
pump for vacuum mattress
an flatable splints set of u in wall anyesic unit.
nitronoy cylinder (light weight)
urinal mole.
ukinal female.
resuscitator complete with cylinder
restraining strap for reuscitator
aspirator manual
first aid kit complete with case bedlpan
tought cut scissors
scissors bandge
vacuum flask stainless steel ilitter
restraining strop for vacuum flasks
oxygen cylinder bull nose (sizef)
oxygen flow meter /regulator
optional equipmens schedule ambulance
clinder
humidifier
oxygen face mack
pulsoxy meter (mini
caphometer (mini)
refloment
hand light (handle projector will rechargarble battery
green bubble 30 foot roll
electronic sphggmomanometer
ultraviolet lamp
02-06-00986 | Deep freezer -80 | [7 empty] | 200
1-vertical type & modile
2-tempertuie from -80c to - 120c
3-capacity :- 26 cutic ft
4-compressor :- single phase (220 / 50/1)
5- alarm system visible & audible
6- thermomter and temperture recorder fixed on the out ar surface of the deep freezer
7-moving dramers stainless steel
8-the frrer sarfacc of the deep freezer shoull be of ron corrosier stanless
9- spare parts recomanedel for five year
10-2doors , stainles (not glass)
02-06-00987 | deep freezer -80 | [7 empty] | 200
1-uprigt freezer new from know company or good traed mark.
2-contain 4 to 6 indepen dent compartment each with an insulating inner door.
3-should be easy programmlg
4-maximum temp. range iN(-80C)
5-temperature stability + 0.5 C in the sample
6- ext. size N 200x80
7-mass kg 200kgm
8- nominal valve lit 300-500 liters
9-capacity sryobox 200 - 400
10-should be power freezer solid construction staliss steel in terior power full reliable stage compressars
11-provided with miwo prolessar control eye level display serve menue for engineer diagnesis door ajar alarmty mult.ple alarms 4 door kag lock
02-06-00988 | Deep freezer | [7 empty] | 200
for ultra low temp. freezer
outer dimension :W2570 XD770 XH1070 MM or equivalent
inner dimension :W1840 XD500 XH672 MM or equivalent
effectve capacity: 700L
exterior : baked -on acrylic finish on galvanized steel
interior : stianless steel
door : baked -on acrylic finish on galvanized steel
insulation :polyurethane foamed in place (NON-CFC)
compressor :hermatic type
motor for compressor :high temp side 1100W low tempside 1100W
evaborator :type on sheet type
condensor :high remp side tube type -low temp side shell tube type
temp - controller : microprocessor conter sys set rang :
(-20 to -120)
(-20 to -95)
with sensor , alarm system, recorder ,back-up system and aluminium container with all accessories
system should be work with power source of AC240V 50 HZ
02-06-00989 | Freezer, - 80C | [7 empty] | 200
the lwo deep freez have the same specification each of them consist of two cooling units deep freeze
unit (1)
electricitey:- 220V - 50V - 1phose
compressor:- 625 w recepeoeating
refrigerant :-502 or R22
FL - current of fan condensor : 0.3A
unit (2)
electricity:- 220V - 50HZ - 1phase
compressor:-425 W receprocating
refrgerant:- 503
bothe the have tow pressure and pressure control temperature of deep freezer is (-80 / -100C)
02-06-00990 | Freezer - 40 C0 | [7 empty] | 200
A- size 14 feet
B-five freezer vertical and five horizontal
C-storage temperature _40
02-06-00991 | Freezer - 120 C0 | [7 empty] | 200
A- size 14 feet
B- vertical type
C-storage temperature _120
02-06-00992 | CCTV | [7 empty] | 200
1- coloured , tilt - pan control facility high resolution , compact size auto iriz auto focus , integrated with operation theaters lamps , camera.
2- coloured , fixed indoor type , wall mounted , standard resolution compact size , auto iriz camera.
3- video matrix switching and recording / control system
a-full cross point video matrix.
b-logical camera selection
c-priority level operation
d-built in video loss detection
e-built in system dignostics
f-windows based system management software complete with central possessing unit (cpu) , matrix switching bay , pwer supply . Key board , printer , monitor , digital video recorders
4-monitor
21 colour high resolution , 100% steel housing front panel control 110 - 240 VAC , built in speaker , video and audis input and out put , automatic colour switching - system ( PAL/NTSC) , front handles facilitate rack mountiog
02-06-00993 | Generator (1MVA) | [7 empty] | 200
230-400v
02-06-00994 | air compressor | [7 empty] | 200
horse power :-15hp
max pressure :-10bar
flow rate :-49.5 cfm / 14001 /m
r . P. m :-1450