## XIII 13-02
SECTION 5-1: DOURA II SEWAGE PUMPING STATION AND DUPLICATE WEST TRUNK SEWER
CODE NO | DESCRIPTION | QTY
13-02-00001 | EXCUTION OF THE DOURA II PUMPING STATION WHICH IS DESIGNED TO
LIFT COMBINED SEWAGE FLOWS FROM THE NEW DUPLICATE WEST TRUNK
SEWER THROUGH TRIPLE RISING MAINS INTO THE KERKH SEWAGE
TREATMENT WORKS THE WORKS INCLUDES THE FOLLOING UNITS
DOURA II PUMPING STATION
INLET DISTRIBUTION CHAMBER
THREE SCREEN CHAMBER WITH MECANICALLY RAKED SCREEN AND
CONVEYORS
MAIN PUMP BUILDING HOUSING, NINE SEWAGE PUMP SETS AND
INCORPORATING WET WELL , DRY WELL , MOTOR ROOM WITH SERVICE ROOM
VALVE CHAMBER ON OUTGOING RISING MAINS
HIGH VOLTAGE SWITCH GEAR AND TRANSFORMER BUILDING
STAND -BY GENERATORS WITH DIESEL STORAGE TANKS
SITEROADWORKS FENCING AND SEIVVCES
DUPLICATE WEST TRUNK SEWER
THE WORKS COMPRISE THE COMPLETE CONSTRUCTION OF A PVC-LINED
IN-SITU CONCRETE TRUNK SEWER INCLUDING MANHOLES , VARYING FROM
2.8M DIA TO 3.6M DIA TOTAL LENGTH 7.3 KM APPROXIMATELY
TRIPLE 1.6 M DIA .DUCTILE IRON RISING MAINS TOTAL LENGTH 4.5 KM
APPROXIMATELY .
THE SCOPE OF THE WORK FOR THE COMELETE CONSTRUCTION OF THE
WORKS AS DETAILD IN THE SPECIFICATION , BILLS OF QUANTITIES AND
DRAWINGS WHICH CAN BE OBTAINED FROM AMANAT BAGDAD.
SECTION 5-2: WATER TREATMENT PLANT WITH A CAPACITY OF 5 MGD
CODE NO. | DESCRIPTION | QTY
13-02-00002 | 1- DISTRIBUTION TANK (CONCRETE TANK)
SOURCE OF THE RAW WATER WILL BE FROM THE NET WORK , THIS TANK WILL RECEIVE WATER AND DISTRIBUTE IT BY GRAVITY TO THE CLARIFIERS
‎2- LAME‎‎LLA ‎‎CLARI‎‎FIER ‎‎TANK ‎‎(CONCRETE TANK) ‎‎:-‎
‎ - MAXIM‎‎UM ‎‎SURFA‎‎CE ‎‎LOAD ‎‎1.0 m/h .‎
‎ - AUTO‎‎MATIC‎‎ALY ‎‎DESLU‎‎DGING ‎‎VALVE‎‎S .‎
‎ - MECHA‎‎NICAL ‎‎RAPID ‎‎MEXER‎‎S FOR ‎‎THE ‎‎COAQU‎‎LANT , ‎‎AND ‎‎HYDRU‎‎LIC ‎‎FLOCC‎‎ULATI‎‎ON .‎
‎ - OVER ‎‎FLOW ‎‎PIPE .‎
‎3- STORA‎‎GE ‎‎TANK ‎‎‎‎(CONCRETE TANK) :-‎
‎CAPACITY ‎‎OF THE ‎‎TANK 200 ‎‎m3 WHICH ‎‎INCLUDES ‎‎:-‎
‎ - MAIN ‎‎VALVE‎‎S ‎‎BETWE‎‎EN ‎‎THE ‎‎CLARIF‎‎IER ‎‎AND ‎‎THE ‎‎S.TANK ‎‎AND ‎‎BETWE‎‎EN ‎‎THE ‎‎S.TANK ‎‎AND ‎‎THE ‎‎FILTER ‎‎PUMPS ‎‎,‎
‎ * OVER ‎‎FLOW ‎‎PIPE‎
‎* DRAIN‎‎AGE ‎‎VALVE‎‎S‎
‎ * LOW ‎‎AND ‎‎HIGH ‎‎LEVEL ‎‎FLOAT ‎‎SWITC‎‎HES‎
‎ * LEVEL ‎‎INDICA‎‎TER‎
‎ * THE ‎‎TANK ‎‎IS ‎‎DIVIDE‎‎D IN ‎‎TWO ‎‎PARTS ‎‎FOR ‎‎MAINT‎‎ENANC‎‎E ‎‎CASE
‎4- FILTE‎‎RS ‎‎PUMP ‎‎STATI‎‎ON‎
‎THIS ‎‎STATION ‎‎CONTAINE‎‎S :-‎
‎1- (3) ‎‎PUMPS ‎‎(2 DUTY + ‎‎1 ‎‎STAND‎‎BY) ‎‎CAPAC‎‎ITY OF ‎‎EACH ‎‎PUMP ‎‎IS ‎‎600 ‎‎m3/h H ‎‎= 40 m , ‎‎HORIZ‎‎ENTAL ‎‎, ‎‎SPLITE ‎‎CASE ‎‎TYPE , ‎‎ALL ‎‎THESE ‎‎PUMPS ‎‎CONNE‎‎CTED ‎‎TO THE ‎‎STORA‎‎GE ‎‎TANK ‎‎BY ‎‎SUCTIO‎‎N PIPE ‎‎ITS ‎‎DIMAT‎‎ER ‎‎DEPEN‎‎DS ON ‎‎THE ‎‎SPECIFI‎‎CATIO‎‎N OF ‎‎THE ‎‎PUMP .‎
‎2- SUCTIO‎‎N ‎‎VALVE ‎‎AND ‎‎PIPES ‎‎FOR ‎‎EACH ‎‎PUMP .‎
‎3- DELIVE‎‎RY ‎‎NON – ‎‎RETUR‎‎N , ‎‎VENTI‎‎NG , ‎‎VALVE‎‎S .B2011 ‎‎FITTIN‎‎GS ‎‎AND ‎‎PIPES .‎
‎4- MANU‎‎METER ‎‎FOR ‎‎EACH ‎‎PUMP .‎
‎5- TWO ‎‎DELEV‎‎ERY ‎‎COLLE‎‎CTOR ‎‎PIPES ‎‎CONNE‎‎CTED ‎‎THROU‎‎GH BY ‎‎PASS ‎‎VALVE ‎‎.‎
‎6- TWO ‎‎MAIN ‎‎BUTTE‎‎R FLY ‎‎ELECT‎‎RICAL ‎‎VALVE‎‎S .‎
‎7- ALL ‎‎THE ‎‎EQUIP‎‎MENTS ‎‎FOR ‎‎THE ‎‎FILTER ‎‎PUMPS ‎‎.‎
‎8- OVER ‎‎HEAD ‎‎ELECT‎‎RICAL ‎‎CRANE ‎‎CAPAC‎‎ITY 2 ‎‎TON ‎‎WITH I ‎‎BEAMS ‎‎, ‎
‎ BRIDGE ‎‎, AND ALL ‎‎THE ‎‎ACCESSOR‎‎IES .‎
‎9- ‎‎ELCTRICA‎‎L BOARD ‎‎WITH ‎‎MAIN ‎‎CIRCUIT ‎‎BREAKERS ‎‎, SOFT ‎‎START – ‎‎STOP ‎‎STARTERS ‎‎CAPACITY ‎‎132 KW ‎‎.
‎5- PRESS‎‎URE ‎‎FILTE‎‎RS ‎‎STATI‎‎ON :-‎
‎THIS ‎‎STATION ‎‎WILL ‎‎INCLUDES ‎‎THE ‎‎FOLLOWIN‎‎G :-‎
‎1- CAPAC‎‎ITY OF ‎‎EACH ‎‎UNIT ‎‎200 ‎‎m3/h , ‎‎FLOW ‎‎RATE 8 ‎‎m3/m2/h ‎‎, ‎‎OPERA‎‎TING ‎‎PRESS‎‎URE 5 ‎‎bar , ‎‎TESTIN‎‎G PRESSURE 10bar ‎‎DISHE‎‎ND ‎‎THICN‎‎ESS 18 ‎‎m m .‎
‎2- MEDIA ‎‎OF ‎‎THE ‎‎FILTER ‎‎3 ‎‎LAYER‎‎S AS ‎‎BELOW ‎‎:-‎
‎ * FIRST ‎‎LAYER ‎‎10 cm ‎‎HEIGH‎‎T SIZE ‎‎3.15 mm ‎‎– 5.6 ‎‎mm ‎
‎* SECAN‎‎D ‎‎LAYER ‎‎15 cm ‎‎HEIGH‎‎T SIZE ‎‎2 mm - ‎‎3.15 mm ‎
‎ * THIRD ‎‎LAYER ‎‎APROX‎‎IMATL‎‎Y 75 ‎‎cm SIZE ‎‎0.8 – ‎‎1.25 mm‎
‎3- FILTER ‎‎UNIT ‎‎WILL ‎‎BE ‎‎INCLU‎‎DED ‎‎THE ‎‎FOLLO‎‎WING ‎‎VALVE‎‎S , ‎‎INLET , ‎‎OUTLE‎‎T , ‎‎DRAIN‎‎AGE , ‎‎RELIFE ‎‎, ‎‎OUTLE‎‎T OF ‎‎BACK ‎‎WASHI‎‎NG , ‎‎INLET ‎‎OF ‎‎BACK ‎‎WASHI‎‎NG ‎‎FOR ‎‎BOTH ‎‎WATER ‎‎AND ‎‎AIR .‎
‎4- INLET ‎‎AND ‎‎OUTLE‎‎T ‎‎MANU‎‎METER ‎‎.‎
‎5- MAINT‎‎ENANS‎‎E ‎‎MANH‎‎UALES ‎‎TWO ‎‎IN THE ‎‎UPPER ‎‎PART ‎‎AND ‎‎TWO ‎‎IN THE ‎‎LOWER ‎‎PART ‎‎OF ‎‎THE ‎‎FILTER ‎‎.‎
‎6- THE ‎‎FILTER ‎‎WILL ‎‎BE ‎‎SKID ‎‎MOUN‎‎TED .‎
‎7- PAINTI‎‎NG OF ‎‎THE ‎‎INTER‎‎NAL ‎‎AND ‎‎EXTER‎‎NAL ‎‎SURFA‎‎CES ‎‎WILL ‎‎BE ‎‎ACCOR‎‎DING ‎‎TO ‎‎THE ‎‎WORL‎‎D ‎‎STAND‎‎ARD ‎‎SPECIFI‎‎CATIO‎‎N .‎
‎8- THE ‎‎TOTAL ‎‎NUMBE‎‎R OF ‎‎THE ‎‎PRESS‎‎URE ‎‎FILTER‎‎S TO ‎‎BE ‎‎FILTER‎‎S ‎‎DIVIDE‎‎D IN ‎‎TWO ‎‎ROWS ‎‎THERE ‎‎ARE ‎‎TWO ‎‎MAIN ‎‎VALVE‎‎S FOR ‎‎EACH ‎‎ROW ‎‎ONE ‎‎FOR ‎‎THE ‎‎INLET ‎‎AND ‎‎THE ‎‎OTHER ‎‎FOR ‎‎THE ‎‎OUT ‎‎LET .‎
‎9- FILTER‎‎D ‎‎WATER ‎‎FOR ‎‎BOTH ‎‎GROUB‎‎S ‎‎CONNE‎‎CTED ‎‎IN ONE ‎‎MAIN ‎‎COLLE‎‎CTOR ‎‎PIPE .‎
‎10- MAIN ‎‎BUTTE‎‎RFLY ‎‎ELECT‎‎RICALL‎‎Y ‎‎OPERA‎‎TED ‎‎VALVE ‎‎.
‎6- ‎‎ALUMINU‎‎M ‎‎SULPHATE ‎‎SYSTEM‎
‎THIS ‎‎SYSTEM ‎‎INCLUDES ‎‎THE ‎‎FOLLOWIN‎‎G :-‎
‎a- PREPA‎‎RATIO‎‎N AND ‎‎SATUR‎‎ATION ‎‎TANKS ‎‎:-‎
‎ - 3 – ‎‎TANKS ‎‎WITH ‎‎CAPAC‎‎ITY 10 ‎‎m3/PER ‎‎TANK , ‎‎MATER‎‎IAL OF ‎‎THE ‎‎TANK ‎‎ANTIC‎‎ORROS‎‎IVE ‎‎FOR ‎‎ALUMI‎‎NUM – ‎‎SULPH‎‎ATE .‎
‎ - THE ‎‎TANKS ‎‎WILL ‎‎BE ‎‎SUPPLI‎‎ED ‎‎WITH ‎‎SERVIC‎‎E ‎‎WATER ‎‎FROM ‎‎THE ‎‎OUTLE‎‎T ‎‎FILTED ‎‎WATER ‎‎LINE .‎
‎ - LADDE‎‎R AND ‎‎WALK ‎‎WAY ‎‎AROUN‎‎DTHE ‎‎TANK .‎
‎ - ELECT‎‎RICAL ‎‎OVER ‎‎HEAD ‎‎CRANE ‎‎WITH ‎‎CAPAC‎‎ITY ‎‎500 Kg .‎
‎ - ELECT‎‎RICAL ‎‎MIXER ‎‎FOR ‎‎EACH ‎‎TANK ‎‎MANUF‎‎ACTUR‎‎ED ‎‎FROM ‎‎STAINL‎‎ESS – ‎‎STEEL ‎‎AND S ‎‎– ‎‎STEEL ‎‎BASKE‎‎T ‎‎CAPAC‎‎ITY ‎‎500 Kg ‎‎AT ‎‎THE ‎‎UPPER ‎‎PART ‎‎OF ‎‎THE ‎‎TANK .‎
‎ - ALUMI‎‎NUM ‎‎SULPH‎‎ATE ‎‎TANKS ‎‎INCLU‎‎DE ‎‎ALL ‎‎THE ‎‎FOLLO‎‎WING :-‎
‎ * INLET ‎‎, ‎‎OUTLE‎‎T , ‎‎DRAIN‎‎AGE , ‎‎OVER ‎‎FLOW ‎‎VALVE‎‎S .‎
* LEVEL ‎‎INDICA‎‎TORS .‎
‎ * METAL‎‎IC ‎‎STRAC‎‎TURE ‎‎WITH ‎‎COVER ‎‎.‎
‎ * LIGHTI‎‎NG .‎
‎b- ALUMI‎‎NUM ‎‎SULPH‎‎ATE ‎‎DOSIN‎‎G ‎‎PUMPS ‎‎AS ‎‎BELOW ‎‎:‎
‎ - NUMBE‎‎R OF ‎‎THE ‎‎PUMPS ‎‎THREE ‎‎PUMPS ‎‎WITH ‎‎CAPAC‎‎ITY 1000 ‎‎L/h ‎‎HEAD ‎‎50 m ‎‎FOR ‎‎EACH ‎‎PUMP .‎
‎C- ‎‎ALUMINU‎‎M ‎‎SULPHATE ‎‎SYSTEM ‎‎INCLUDES ‎‎ALL THE ‎‎UPVC ‎‎PIPES , ‎
‎ VALVES ‎‎, FITTINGS ‎‎, ‎‎PULSATER ‎‎DAMPNER , ‎‎MANUMET‎‎ERS , TWO ‎
‎ ‎‎ADJUSTAB‎‎LE ‎‎FLOWMET‎‎ER , TWO ‎‎MAIN ‎‎DISCHARG‎‎E PIPES ‎‎WHICH ‎
‎ MUST ‎‎BE ‎‎CONNECTE‎‎D TO THE ‎‎INJECTION ‎‎POINTS ‎‎OF ‎‎THE ‎
‎ ‎‎FLOCCULA‎‎TION TANK ‎‎.
‎7- ‎‎CHLORIN‎‎ATION ‎‎STATION ‎
‎CHLORINE ‎‎GAS WILL ‎‎BE USED ‎‎FOR THE ‎‎DISINFECT‎‎ION SO IT ‎‎SHALL BE ‎‎INJECTED ‎‎AT THE ‎‎STORAGE ‎‎TANK ‎‎AND THE ‎‎INLET OF ‎‎THE ‎‎LAMELLA ‎‎TANK AS ‎‎PRE – ‎‎CHLORINA‎‎TION AND ‎‎ALSO ‎‎WILL BE ‎‎INJECTED ‎‎AT THE ‎‎OUTLET ‎‎OF THE ‎‎PRESSURE ‎‎FILTERS ‎‎AS POST – ‎‎CHLORINA‎‎TION , THIS ‎‎STATION ‎‎INCLUDES ‎‎THE ‎‎FOLLOWIN‎‎G :-‎
‎ - 3 ‎‎CHLOR‎‎INATO‎‎RS ‎‎CAPAC‎‎ITY 5 ‎‎Kg/h ‎‎FOR ‎‎EACH ‎‎UNIT .‎
‎ - 3 ‎‎INJECT‎‎ERS .‎
‎ - 1 ‎‎CHANG‎‎E ‎‎OVER ‎‎DEVIC‎‎E .‎
‎ - 1 LEAK ‎‎DETEC‎‎TOR .‎
‎ - 2 ‎‎HEADE‎‎RS ‎‎WITH ‎‎ALL ‎‎THE ‎‎INLET ‎‎AND ‎‎OUTLE‎‎T ‎‎VALVE‎‎S .‎
‎ - 50 ‎‎FLEXIB‎‎LE ‎‎PIPES ‎‎BETWE‎‎EN ‎‎THE ‎‎CYLIN‎‎DERS ‎‎AND ‎‎THE ‎‎HEADE‎‎RS (5 ‎‎DUTY + ‎‎45 ‎‎SPARE‎‎S) .‎
‎ - 3 PRV .(1 DUTY + 2 STAND BY)
‎ - 3 ‎‎CATCH ‎‎POT .‎
‎ - WATER ‎‎AND ‎‎GAS ‎‎MANU‎‎METER‎‎S .‎
‎ - 3 ‎‎BOOSTI‎‎NG ‎‎PUMPS ‎‎CAPAC‎‎ITY 4 ‎‎m3/h , H ‎‎= 80 m ‎‎FOR ‎‎EACH ‎‎WITH ‎‎ALL ‎‎THE ‎‎PIPES , ‎‎VALVE‎‎S , NON ‎‎– ‎‎RETUR‎‎N ‎‎VALVE‎‎S , ‎‎FITTIN‎‎GS .‎
‎ - ALL ‎‎THE ‎‎FITTIN‎‎GS , ‎‎PIPES , ‎‎VALVE‎‎S , ‎‎INJECT‎‎ION ‎‎POINTS ‎‎.
‎8- AIR ‎‎BLOWER ‎‎SYSTEM‎
‎THE ‎‎SYSTEM ‎‎INCLUDES ‎‎THE ‎‎FOLLOWIN‎‎G :-‎
‎-3 – AIR ‎‎BLOWERS . ‎‎THE ‎‎REQUIRED ‎‎FLOW ‎‎RATE ‎‎WILL BE ‎‎60 m3/ m2 /H ‎‎DURING ‎‎THE ‎‎SQUENCE ‎‎OF BACK ‎‎WASHING ‎‎THE ‎‎FILTER ‎‎WITH AIR ‎‎BLOWER .‎
‎ - ALL ‎‎THE ‎‎VALVE‎‎S FOR ‎‎THE ‎‎INLET , ‎‎OUTLE‎‎T , NON ‎‎– ‎‎RETUR‎‎N , ‎‎INLET ‎‎FOR ‎‎EACH ‎‎FILTER ‎‎, PIPES , ‎‎MANU‎‎METER‎‎S , ‎‎FITTIN‎‎GS .
‎9- BACK ‎‎WASHING ‎‎WATER ‎
‎THE ‎‎REQUIRED ‎‎FLOW ‎‎RATE FOR ‎‎THE BACK ‎‎WASHING ‎‎WITH ‎‎WATER ‎‎MUST BE NOT LESS ‎‎30 m3/ m2 /h ‎‎THIS CAN ‎‎BE ‎‎CREATED ‎‎MAINLEY ‎‎THROUGH ‎‎BRANCH ‎‎FROM THE ‎‎MAIN ‎‎FILTERD ‎‎WATER ‎‎AND BY ‎‎USING ‎‎HORIZONT‎‎EL PUMPS ‎‎(AS ‎‎OPTION) .
‎10- ‎‎GENERAT‎‎OR ‎‎STATION‎
‎ - 1 ‎‎STAND ‎‎BYE ‎‎GENER‎‎ATOR ‎‎0.4 KV , ‎‎1000 RPM , ‎‎50 HZ .‎
‎ - CAPACITY ‎‎360 ‎‎KVA ‎‎(PRIME‎‎) .‎
‎ - INCLU‎‎DE ‎‎ALL ‎‎ACCES‎‎SORIES ‎‎, ‎‎WATER ‎‎COOLI‎‎NG ‎‎SYSTE‎‎M ‎‎RADIA‎‎TORS , ‎‎OIL ‎‎LUBRI‎‎CATIO‎‎N ‎‎PUMPS ‎‎, FUEL ‎‎TANKS ‎‎FOR 48 ‎‎HOURS ‎‎DUTY , ‎‎UPS ‎‎CHARG‎‎ER ‎‎AND ‎‎BATTE‎‎RIES 10 TON CHLORINE DRUM STORE WITH 2 TON OVER HEAD CRANE
‎ - WITH ‎‎ITS ‎‎ELECTRIC‎‎AL ‎‎SWITCH ‎‎BOARD ‎‎CONSIST ‎‎OF ‎‎CIRCUITS ‎
‎ ‎‎BREAKERS ‎‎, AND ‎‎SERVICES ‎‎SWITCH ‎‎BOARD .
‎11-‎‎ELECTRIC‎‎ITY ‎‎POWER‎
‎SPECIFICA‎‎TIONS OF ‎‎THE ‎‎EQUIPMEN‎‎TS WHICH ‎‎REQUIRED ‎‎FOR ‎‎ ‎‎WTP WILL ‎‎BE AS ‎‎BELOW :-‎
‎a- HIGH ‎‎TENTIO‎‎N ‎‎BOARD ‎
‎ - 2 ‎‎INCOM‎‎ING ‎‎FEEDE‎‎RS + ‎‎ONE ‎‎BUS – ‎‎COUPL‎‎ERS (11 ‎‎KV , ‎‎630 A) .‎
‎ - 2 OUT ‎‎GOING ‎‎(11 KV , ‎‎630 A) ‎‎TO ‎‎THE ‎‎TRANS‎‎FORME‎‎RS .‎
‎b- 2 ‎‎TRANS‎‎FORME‎‎RS (11 ‎‎KV/0.4 ‎‎KV) ‎‎CAPAC‎‎ITY OF ‎‎EACH ‎‎ONE 400kVA .‎
‎c- LOW ‎‎TENTIO‎‎N ‎‎BOARD ‎‎(400 V , ‎‎50 c/s) ‎‎INCLU‎‎DES ‎‎THE ‎‎FOLLO‎‎WING :-‎
‎ - 2 MAIN ‎‎CIRCUI‎‎T ‎‎BREAK‎‎ERS ‎‎(400 V , 800 A , ‎‎50 c/h) .‎
‎ - 1 MAIN ‎‎CIRCUI‎‎T ‎‎BREAK‎‎ERS ‎‎(400 V , 800 A , ‎‎50 c/h FOR GENERATOR ) .‎
‎ - 1 BUS – ‎‎COUPL‎‎ERS ‎‎(400 V , 800 A , ‎‎50 c/h) .‎
‎ - 5 ‎‎CIRCUI‎‎T ‎‎BREAK‎‎ER ‎‎(630A)‎ (3 CB FOR 132 KW STARTARS + 2 SPARES)
‎ - 5 ‎‎CIRCUI‎‎T ‎‎BREAK‎‎ER ‎‎(100A)‎
‎ - 3 ‎‎CIRCUI‎‎T ‎‎BREAK‎‎ER ‎‎(50A)‎
‎d- SOFT ‎‎STARTERS ‎‎, BOARDS‎
‎ - 5 SOFT ‎‎START ‎‎– STOP ‎‎START‎‎ERS ‎‎(132 ‎‎KW) .(2 STAND BY)
‎ - 1 ‎‎BOARD ‎‎INVOL‎‎VES ‎‎THREE ‎‎START‎‎ERS ‎‎FOR ‎‎THE ‎‎AIR ‎‎BLOWE‎‎RS ‎‎ACCOR‎‎DING ‎‎TO ‎‎THE ‎‎BLOWE‎‎RS ‎‎SPECIFI‎‎CATIO‎‎NS .‎
‎ - 1 ‎‎BOARD ‎‎FOR ‎‎ALL ‎‎THE ‎‎UXILL‎‎ARY ‎‎EQUIP‎‎MENTS ‎‎LIKE ‎‎OVER ‎‎HEAD ‎‎CRANE ‎‎, ‎‎FLOCC‎‎ULATO‎‎RS , ‎‎ELECT‎‎RICAL ‎‎VALVE‎‎S , ‎‎LIGHTI‎‎NGS , ‎‎MIXER‎‎S , ‎‎VENTE‎‎LATOR‎‎S , AIR ‎‎CONDI‎‎TIONE‎‎RS , ‎‎FLOW‎‎METER‎‎S .‎
‎ - 1 ‎‎BOARD ‎‎FOR ‎‎THE ‎‎CHLOR‎‎INATIO‎‎N ‎‎STATIO‎‎N ‎‎WHICH ‎‎INVOL‎‎VES ‎
‎ 3-‎‎STARTERS ‎‎FOR THE ‎‎BOOSTING ‎‎PUMPS , ‎‎AND ALL ‎‎OTHER ‎
‎ ‎‎ACCESSOR‎‎IES .‎
‎ - 1 ‎‎BOARD ‎‎FOR ‎‎THE ‎‎ALUMI‎‎NUM ‎‎SULPH‎‎ATE ‎‎SYSTE‎‎M ‎‎WHICH ‎‎INCLU‎‎DES :-‎
‎ * ‎‎START‎‎ERS ‎‎FOR ‎‎THE ‎‎MIXER‎‎S .‎
‎ * ‎‎START‎‎ERS ‎‎FOR ‎‎THE ‎‎DOSIN‎‎G ‎‎PUMPS ‎‎.‎
‎ * ‎‎STARTE‎‎R FOR ‎‎THE ‎‎OVER ‎‎HEAD ‎‎CRANE ‎‎AND ‎ ‎ALL ‎‎ OTHER ‎‎ ACCESS‎‎ORIES‎
‎ * GENERAL NOTES :-‎
‎1- ALL THE BOARD INCLUDE ALL PROTECTIONS AND INTERLOCKS SUCH AS UNDER VOLTAGE , ‎‎SHORT CIRCUIT , OVER LOAD THERMOSTATE PROTECTION OF MOTORS ECT , METERS ‎‎VOLTMETER , BULBS .‎
‎2- THE LOW VOLTAGE (STARTERS OF MOTORS) INCLUDE POWER FACTOR CORRECTION UNIT UP TO ‎‎0.9 .‎
‎3- RECALCULATE THE LOAD FOR BETTER DESIGN .‎
‎4- THE OFFER SHOULD INCLUDE ALL EQUIPMENT AND ACCESSORIES SUFFICIENT TO OPERATE THE ‎‎PLANT PROPERLY .‎
‎5- GIVE AS OPTIONS IF THERE ARE BETTER OR MODERN EQUIPMENTS SUITABLE FOR PLANT .‎
‎6- RECHECK CALCULATION AND SPECIFICATIONS ACCORDING TO HIGH STANDARDS AND GIVE AS ‎‎YOUR COMMENTS .‎
‎7- THE OFFER SHOULD INCLUDE INSTALATION AND ERECTION OF ALL BUILDINGS INCLUDING ‎‎CONCRETE WORK .‎
‎8- SPARE PARTS FOR 2 YEARS OF OPERATION (ITEMIZED SPARE PARTS)‎
‎9- SUPPLIER RESPOSIBILITIES ARE :-‎
‎a- ERRECTION AND INSTULATION OF ALL THE EQUIPMENTS .‎
‎b- SUPPLYING AND INSTALLATION HOUSES FOR ALL THE ‎‎STATIONS AND THE SYSTEMS .‎
‎10- THE OFFER INCLUDES ALL THE CABLES BETWEEN THE ELECTRICAL EQUIPMENTS .‎
11- THE OFFER INCLUDES ALL THE INTER CONNECTION PIPES BETWEEN ALL THE STATIONS.